Diagnostic Results of Power Transformers' Technical Condition Based on Chromatographic Analysis of Gas Concentrations and Moisture Content in Oil

Dilmurod Yusupov1, a), Asrorbek Nosirov1, b), Khilola Khamrakulova2, c), 
Kambarali Ahunov2, d), Abdullajon Khomidov2, e) and Kutbidinov Odiljon3, f)

1Institute of Energy Problems, Academy of Sciences of the Republic of Uzbekistan, Tashkent 100095, Uzbekistan
2Fergana State Technical University, Fergana 150107, Uzbekistan
3Tashkent State Transport University, 1 Temiryulchilar St., Tashkent 100167, Uzbekistan

a) Corresponding author: dilmurod85@list.ru
b) asrorbeknosirov6210@gmail.com
c) hamrokulovahilola84@gmail.com
d) Kambarali.ahunov.@ferpi.uz
e) abdullajon.xomidov@ferpi.uz 
f) odiljon.qutbidinov@bk.ru

Abstract. This article covers the results of diagnostics based on the gas content and humidity level of transformer oil in assessing the technical condition of power transformers. The research was carried out in the laboratory of the diagnostic enterprise “TEXenergoremmash”. Through the gas chromatography method, three high voltage transformer oil samples were studied, analyzing the mass fraction, relative concentration, growth rate, and potential defect symptoms of gases. During the analysis, two chromatograph devices of “Kristalluks-4000m” were applied, and work was carried out on the basis of the requirements of the regulatory document GOST 26703-93. Based on the results obtained, specific recommendations for assessing, forecasting and monitoring the technical condition of transformers were developed.

Keywords: power transformer, oil, technical condition, gas analysis, humidity, chromatographic analysis, diagnostics

INTRODUCTION

One of the important factors in the reliable and safe operation of power transformers today is to maintain their technical condition in constant control. Especially in long-running high-voltage transformers, processes such as insulation system degradation, internal heating processes, and electrical arcs can cause significant failures over time [1, 2]. One of the most effective tools for early detection and Prevention of these conditions is the analysis of gases dissolved in transformer oil and the assessment of the amount of moisture.

This research was carried out in the laboratory of the texenergoremmash diagnostic enterprise, in which a technical condition was analyzed based on oil samples from power transformers [6, 7, 8]. The tests were carried out using two gas chromatograph devices of the type “Kristalluks-4000m”, based on the requirements of the regulatory document GOST 26703-93. The experiment found major gases that were dissolved in transformer oil (H2, CH4, C2H2, C2H4, C2H6, CO, CO2) as well as indicators of moisture and predicted the possible defects due to their quantitative change [3, 4, 5].

Based on the results obtained in this article, recommendations are presented for an effective assessment of the technical condition of transformers, as well as the development of planned diagnostic measures [9, 10].

RESEARCH MATERIALS AND METHODS

The study was carried out in the laboratory of the Enterprise “Texenergoremmash”, in which, using chromatograph measuring devices “Kristalluks-4000m”, gases contained in oil samples of several power transformers were injected based on the regulatory document GOST 26703-93.

Headings, Tables and Figures

High voltage oil power transformers have been selected for analysis as a research object (Table 1).

TABLE 1. Data about Transformers these samples come from

| Equipment type | Capacity (kVA) | Voltage (kV) | Year of operation |
| --- | --- | --- | --- |
| Oil power transformer | 11000 | 35/10 | 2007 |
| Oil power transformer | 11000 | 35/10 | 2021 |
| Oil power transformer | 11000 | 35/10 | 2007 |

A sample of oil with a volume of 1 liter from a power transformer is taken into a special clean and dry container and prepared for chromatographic analysis.

The study was carried out using the method of chromatographic analysis of gases (XARG). The following main gases contained in the oil have been identified and analyzed:

- carbon monoxide (CO);

- carbon dioxide (CO2);

- acetylene (C2H2);

- hydrogen (H2);

- methane (CH4);

- ethylene(C2H4);

- ethane (C2H6).

These gases get formed when there are thermal or electrical discharges within the system of insulation and shrinkage of the transformer.

The experimental study was performed on a modern chromatograph measuring pribar Figure 1 of the “Kristalluks-4000m” type. The measuring pribar has high accuracy, allowing for the detection of microgrammic level gases in the oil. Device is equipped with a system for automatically comparing samples against each other, gas separation and processing data in digital form.

FIGURE 1. Modern “Kristalluks-4000M” chromatographic measuring device

The main technical indicators of the “Kristalluks-4000m” measuring pribar:

Temperature range: +5 °C to +400 °C;

Temperature setting accuracy: ±0.1 °C;

Cooling rate: 400 °C-100 °C (in 5 minutes);

Gas carrier flow: 0.5-100 ml/min;

Pressure range: 0.005-0.40 MPa;

Power supply: 220 V, 50 Hz, 900 and

Dimensions: 550×500×500 mm;

Weight: 39 kg;

Detector sensitivity (FID): 5×10-13 g/s (per benzene).

FIGURE 2. Chromatograph device that determines the concentration of water and gas in the oil “Kristalluks-4000M”

| FIGURE 3. Oil samples | FIGURE 4. Special syringes to place samples on a chromatograph |
| --- | --- |

FIGURE 5. Device for stirring the oil sample infused with argon gas

Research Objective

The aim of the research is to diagnose the technical condition of power transformers based on gas analysis of the insulating oil.

Oil samples were analyzed using “Kristalluks-4000M” chromatographic measuring devices in accordance with the GOST 26703-93 standard. Initially, the oil samples were delivered in clean and dry special containers Figure 3. The measuring vessel of the device Figure 4 was rinsed twice with the sample and then filled with 100 ml of transformer oil.

Argon gas was then introduced through the inlet and outlet tubes of the measuring device Figure 1, followed by 10 minutes of mixing using a stirrer Figure 5. The measuring device analyzes the gases dissolved in the oil sample through its intake tubing. Simultaneously, the second chromatographic measuring device Figure 2 determines the moisture content and gas concentrations in the oil sample and transmits the data to the first chromatograph Figure 1. These two devices operate in an integrated mode.

The software of the devices transfers the collected data to a computer. Based on the ratio of moisture and gas concentrations, the automated diagnostic system on the computer generates conclusions and recommendations without human interference.

Research Results and Their Analysis

Oil samples taken from high-voltage power transformers were analyzed using the “Kristalluks-4000M” chromatographic measuring device. The content of dissolved gases, moisture levels, and gas concentrations in the oil were determined, serving as a basis for evaluating the technical condition of the transformers. Dissolved gases, moisture and gas content within the oil were measured and used as the criteria of determining the technical state of the transformers. The software that conducted the condition assessment did not do so under the influence of human control and gave out automated diagnostic conclusions. The measurement outcomes, as well as the conclusions made by the program are provided below.

| a) Sample 1 – Diagnostic Summary | b) Sample 2 – Diagnostic Summary |
| --- | --- |
| c) Sample 3 – Diagnostic Summary |  |

FIGURE 6. Dynamics of changes in moisture content and dissolved gas concentrations in transformer oil samples

TABLE 2. Moisture Content and Gas Concentration in High-Voltage Power Transformer Oil Samples

| Composition of Sample 1 |  |  |  |  |
| --- | --- | --- | --- | --- |
| № | Component | Mass Fraction, % |  | Moisture Content, gr/t |
| 1 | Gas Concentration | 16,9114 |  | 169113,52 |
| 2 | Moisture Content | 0,0011 |  | 10,74 |
| Total: |  | 16,9124 |  | 169124,26 |
| Composition of Sample 2 |  |  |  |  |
| 3 | Gas Concentration | 18,7760 |  | 187760,47 |
| 4 | Moisture Content | 0,0011 |  | 10,54 |
| Total: |  | 18,7771 |  | 187771,01 |
| Composition of Sample 3 |  |  |  |  |
| 5 | Gas Concentration | 18,4203 |  | 184202,75 |
| 6 | Moisture Content | 0,0011 |  | 10,53 |
| Total: |  | 18,4213 |  | 184213,29 |
| a) Sample 1 – Diagnostic Summary |  |  | b) Sample 2 – Diagnostic Summary |  |  |
| c) Sample 3 – Diagnostic Summary |  |  |  |  |  |

FIGURE 7. Diagnostic conclusion from the “Kristalluks-4000M” chromatographic measuring device for oil samples taken from high-voltage power transformers

Conclusion for Sample 1:

The dissolved gases in the transformer oil do not give conclusive limits that surpass the threshold limits. No increase in gas concentrations has been observed.

| Gas Ratios: C2H2/C2H4 = 0 CH2/H2 = 2,3965 C2H4/C2H6 = 23,907 CO2/CO = 18,977 | Status of Gases: H2 – Non-indicative gas CH4 – Non-indicative gas C2H4 – Non-indicative gas C2H6 – Non-indicative gas C2H2 – Not present CO – Indicative gas, but in low concentration CO2 – Main gas |
| --- | --- |

Potential Defects:

Indicated by gases: No defect found

Recommendations and Comments:

Monitoring should be conducted regularly every 6 months.

Conclusion for Sample 2:

There is a likelihood of a rapidly developing defect.

According to the growth rate:

The relative growth rate of CH₄ gas is 14.819% per month.

| Gas Ratios: C2H2/C2H4 = 0 CH4/H2 = 3,0577 C2H4/C2H6 = 33,764 CO2/CO = 17,386 | Status of Gases: H2 – Non-indicative gas CH4 – Non-indicative gas C2H4 – Non-indicative gas C2H6 – Non-indicative gas C2H2 – Not present CO – Indicative gas, but in low concentration CO2 – Main gas |
| --- | --- |

Potential Defects:

Indicated by gases: No defect found

Recommendations and Comments:

Appointment of monitoring after 6 months should be done.

Operating conditions of the equipment are supposed to be examined with possible consideration of the dynamics of growth recorded in the former sample.

Sample testing should be continued according to the established intervals.

Electrical tests should be performed.

If no issues are identified during the electrical tests, the transformer should not be transferred to enhanced monitoring mode.

Conclusion for Sample 3:

There is a likelihood of a rapidly developing defect.

Based on the growth rate:

The relative growth rate of C₂H₄ is 17.822% per month

The growth rate of C₂H₆ is 13.985% per month.

| Gas Ratios: C2H2/C2H4 = 0 CH4/H2 = 1,421 C2H4/C2H6 = 35,125 CO2/CO = 23,166 | Status of Gases: H2 – Non-indicative gas CH4 – Non-indicative gas C2H4 – Non-indicative gas C2H6 – Non-indicative gas C2H2 – Not present CO – Indicative gas, but in low concentration CO2 – Main gas |
| --- | --- |

Possible Defects:

Based on the indicative gases, the defect cannot be predicted in advance

Recommendations and Notes:

Carry out regular checks after every 6 months. Examine the conditions under which the equipment has to work during the period between the samples

Repeat sampling on the basis of recommended interval

Perform electrical testing

In case of faults identified in the process of electrical testing, the transformer ought to be frequently monitored.

CONCLUSION

During the study, in order to assess the technical condition of high-voltage power transformers, the concentrations of gases and moisture content in transformer oil were analyzed using “Kristalluks-4000M” chromatographic devices. The tests were carried out in accordance with the requirements of the GOST 26703–93 standard. The obtained results made it possible to draw the following key conclusions:

Sample 1: The concentrations of the gases were relatively low with no suggestive gases of any fault identified. The technical condition was evaluated as taking place at the level, and the regular observation should be done after 6 months.

Sample 2: The increasing growth rate of CH₄ and the presence of C₂H₄ indicate the possible occurrence of internal thermal processes. This condition requires strengthened control and attention. Electrical testing is recommended.

Sample 3: Sample 3: C2H4 and C2H6 are showing high relative growth rates, which means there is a probability the fault is developing fast internally.

Moisture Content Analysis:

Transformer oil with moisture content has adverse impacts on dielectric strength viscosity of both liquid and solid insulation is reduced making it prone to overheating and cracking. The moisture level was in vicinity of 10.51-10.7 g/t in all the three samples which is more (acceptable limit is 5 cm/t or less) than the stipulated value (the ideal transformer oil is supposed to have 5 cm/t or less) [2-5]. Very moist levels of all transformers can be signs of damaged hermetic sealing or working in moist areas in not properly dried conditions. The damage to dielectric can lead to the decreased breakdown voltage when performing high-voltage tests. there is also an augmented risk of localized electrical breakdown caused by water vapor.

Recommendations:

For Sample 1:

To lower moisture content in the oil, it is advised to dry (e.g., vacuum drying);

Although gas concentrations are not critical, regular monitoring should be continued.

For Samples 2 and 3:

A more detailed DGA (Dissolved Gas Analysis) should be conducted—especially focusing on acetylene and the CO₂/CO ratio;

Thermodynamic assessment of insulation and inspection of the cooling system is necessary;

Moisture removal procedures such as degassing and oil regeneration should be implemented urgently.

To conclude, chromatographic analysis of the dissolved gases and moisture can be seen as an efficient tool of the evaluation of the technical condition of transformers at an early stage and detection of faults. This strategy improves the quality of diagnosing as well as operating safety of power transformers.

REFERENCES

- O. V. Shutenko, Bull. Kharkiv Petro Vasylenko Natl. Tech. Univ. Agric. 1, 45 (2008). (Ukr).

- I. V. Davidenko, Diagnostic Systems for High-Voltage Oil-Filled Power Electrical Equipment (USTU-UPI, Yekaterinburg, 2003), p. 117.

- O. S. Melnikova, Diagnosis of the Main Insulation of Oil-Filled Power Transformers Based on the Statistical Criterion of Oil Dielectric Strength, Cand. Sci. Dissertation Abstract (Ivanovo, 2015).

- A. G. Stepanov, Assessment and Forecasting of the Insulation System Condition of Power Transformers in Main Electrical Networks, Cand. Sci. Dissertation Abstract (Krasnoyarsk, 2005).

- I. V. Davidenko, Assessment of the Technical Condition of Power Transformers Based on the Results of Traditional Tests and Measurements (UrFU, Yekaterinburg, 2015).

- A. V. Krekhova, Acoustic Control Method for Operational Performance Indicators of Transformer Oils, Cand. Sci. Dissertation Abstract (Krasnoyarsk, 2019).

- NP “INVEL,” Energy Oils and Oil Management Systems of Power Plants and Grids: Operation and Maintenance Norms and Requirements, STO 70238424.27.100.053-2013 (2013), p. 163.

- O. V. Shutyenko, Bull. NTU “KhPI” 44, 162 (2008).

- I. V. Davidenko, V. P. Golubev, V. I. Komarov, V. N. Osotov, and S. V. Turkevich, Energetik 11, 52 (2000).

- C. H. Liu, L. T. Yao, T. B. Lin, and S. Y. Wang, Appl. Mech. Mater. 284-287, 1082 (2013). https://doi.org/10.4028/www.scientific.net/amm.284-287.1082