Prognostic Analysis of Electrical Load and Power Supply Parameters for a Newly Electrified Railway Section Supplied by a Terminal Substation

Ildar Bayanov1, a), Timur Badretdinov1, b), Khayotjon Kurbanov1, c) and 
Ansagan Suleimenov2, d)

1Tashkent State Transport University, 1 Temiryulchilar St., Tashkent 100167, Uzbekistan
2Toraighyrov University, 64 Lomov St., Pavlodar, Kazakhstan

a) Corresponding author: ildar-lili@yandex.ru
b) timurbadretdinov2107@gmail.com
c)qurbonovhayot85@gmail.com
d) ansar_muslim_91@mail.ru

Abstract. The article presents the results of calculations of current consumption, voltage losses, and energy consumption on the electrified section of the Samarkand – Urgut railway, which is powered by the Jambay traction substation. Various types of electric locomotives are considered, as well as their operation modes in single and opposing directions. Particular attention is paid to the evaluation of voltage drop at the current collectors and compliance with the requirements of regulatory documents. The obtained calculation data can be used in the development of power supply projects and optimization of traffic schedules on the section, as well as in the design of the 27.5 kV outdoor switchgear bay, selection of secondary circuits, and configuration of relay protection settings.

Keywords: Railway electrification, catenary system, electric locomotive, pantograph, voltage, power, traction load

INTRODUCTION

Rail transport is one of the most important sectors of our national economy. The role of railways is significantly increasing under market conditions, as their performance directly affects the speed or delay of passenger and freight delivery, the turnover rate of capital, the cost of industrial and agricultural products, and so on. In order to meet growing demand while reducing fuel costs, newly constructed railway sections are currently being electrified. The electrification of railways in Uzbekistan began relatively late compared to a number of other countries, but from the very beginning it was accompanied by the search for effective technical solutions. The first electrified railway line was commissioned in 1971 on the Khavast–Syrdarya section, and at that stage, power supply was provided by a direct current system with a voltage of 3 kV. This system was selected in accordance with the standards of the former Soviet Union, which were particularly effective for relatively short sections with intensive traffic.

However, as the railway network expanded and the length of electrified sections increased, it became clear that the direct current system had a number of limitations — primarily in terms of significant energy losses at traction substations and the limited distance between them. Therefore, in 1985, a strategic decision was made to switch to a more efficient power supply system — single-phase alternating current with a voltage of 27.5 kV and a frequency of 50 Hz. The first section where this new system was implemented was the Keles- Jambai line.

The transition to alternating current significantly improved the energy efficiency of railway traction, allowed for longer distances between substations, and simplified connection to the national power grid [1, 2, 3]. However, from the very beginning of railway electrification — both in Uzbekistan and worldwide — one of the key technical challenges has been the quality of electrical power in the traction system. This is due to the fact that the traction load is typically single-phase, while the main power supply networks are three-phase. Such imbalance results in the appearance of negative sequence currents (NSC) [4, 5, 6, 7], equal in magnitude to positive sequence currents (PSC), which can negatively impact the stability and reliability of the power system [8, 9, 10].

Previously, single-phase commutator motors were used in rolling stock, but since the late 20th century, Uzbekistan, like many other countries, has been implementing more modern traction drives using single-phase rectifiers and three-phase inverters. These devices operate with asynchronous or synchronous traction motors, provide regenerative braking, and allow energy to be returned to the overhead line, increasing the overall efficiency of the power supply system.

Railway electrification has a noticeable impact not only on the power grid but also on other infrastructure elements: upstream power supply networks (high-voltage transmission lines), signaling, communication, and telecommunication systems. Electromagnetic interference caused by traction loads requires special solutions for shielding, grounding, and filtering. Therefore, research is also being carried out in Uzbekistan to improve power quality, reduce electromagnetic and harmonic distortions, and enhance the reliability of traction substations and rolling stock [11, 12, 13].

As part of the analysis of traction load reliability on the electrified section, the design features of locomotives operated in Uzbekistan were studied. Particular attention was given to the rigid double-helical gear transmission, which ensures smooth operation and reduced dynamic loads due to gradual meshing and axial displacement of the gears [14, 15, 16, 17].

Under high load conditions determined through traction calculations, it is especially important to consider the technical condition of the overhead contact system and its supporting structures, as these factors directly affect the reliability of power supply and the safety of train operations. Even a brief detachment of the pantograph can lead to the formation of a high-temperature electric arc, which may cause the wire to burn out and result in an emergency train stop. This electric arc forms within milliseconds, is accompanied by high-frequency magnetic interference, and its formation depends on several factors, including atmospheric pressure, ambient temperature, and the distance between the pantograph and the contact wire [18, 19, 20].

The development of Uzbekistan's railway infrastructure requires improving the efficiency of power supply to new sections. One such section is the Samarkand – Urgut line, whose electrification is carried out using power from the traction substation (TSS) Jambay. At the request of JSC “Uzbekistan Railways”, a working design project is being developed for the construction of a new electrified railway line Samarkand–Urgut. This new railway line, with a total length of 55 km, connects to the existing Tashkent–Samarkand railway line at the Jambay–Zarafshan section. The purpose of this work is to analyze the possibility of supplying the section from the mentioned TSS under various operational train traffic scenarios. The calculations allow for proper current distribution across the section and efficient scheduling of train movement.

### METHODOLOGY AND INITIAL DATA

A properly conducted study is the key to the high-quality and efficient operation of the railway section and ensures significant savings in energy resources. The study was carried out in accordance with the assignment of JSC "Uzbekistan Temir Yullari" taking into account the recommendations of the locomotive operation department, according to which the following electric locomotives can be operated on the section:

- 3ES5K

- 3VL80s

- VL60K

- O‘Z-ELR

- O‘z-Y

However, it is not necessary to limit the analysis to only these types of locomotives, as there is a growing trend toward the use of more energy-efficient electric locomotives and electric trains produced by modern manufacturers.

On the projected section, the catenary system includes a carrying cable PBSM-95 and a contact wire MF-100. The traction rails used on the section are of type Р65. Calculations were performed based on the nominal catenary voltage of 25 kV. The maximum permissible catenary voltage should not exceed 29 kV. Such a voltage value under cantilever feeding and a nominal substation bus voltage of 27.5 kV is practically unachievable.

The parameters of electric locomotives (weight, power, speed, voltage operating range, and current consumption) are shown in Table I. A train mass of 1050 t for passenger trains and 4200 t for freight trains was assumed in the calculations.

TABLE 1. Main parameters of the used electric locomotives

| Parameter | Type of electric locomotive |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | OZ-Y | OZ-ELR | 3ES5K | 3VL80s | VL60K |
| Weight (t) | 126 | 138 | 288 | 280 | 135 |
| Power (kW) | 6000 | 7200 | 9840 | 9240 | 6000 |
| Design speed (km/h) | 160 | 120 | 110 | 110 | 120 |
| Operating voltage range (kV) | 17,5-31 | 17,5-31 | 19 – 29 | 19 – 29 | 19 – 29 |
| Accepted current consumption (A) | 316 cosφ=0.9 | 360 cosφ=0.9 | 314 cosφ=0.8 | 295 cosφ=0.8 | 180 cosφ=0.8 |

Note: Train weights assumed: passenger – 1050 t; freight – 4200 t.

The parameters of newly developed locomotives are usually more energy-efficient while maintaining the same traction characteristics. If modern locomotives are used, the calculations performed can fully meet their operational requirements.

The «Jambay» traction substation (110/27.5/10 kV) is a terminal-type facility, supplying two 27.5 kV feeders in the direction of Tashkent and two feeders toward Zarafshan station. It receives power from two 110 kV transmission lines feeding two 40 MVA traction transformers. In connection with the planned construction of a new 55 km electrified railway section to Urgut, it is necessary to install an additional 27.5 kV outdoor switchgear bay. To justify the selection of the required primary and secondary equipment for this new bay, a traction power calculation must be performed as part of the technical and economic feasibility study.

FIGURE 1. 27.5 kV Outdoor Feeder Bay of the Overhead Contact System at «Jambay» TSS

SCENARIOS CONSIDERED IN THE CALCULATIONS

#### One Locomotive on the Section

To assess power supply parameters, calculations of currents and voltages at the pantograph were performed for single train movements in both directions. Results are presented in Tables II and III. The maximum power consumption ranged from 4300 to 9071 kW, and pantograph voltages ranged from 19 to 25 kV depending on the locomotive type and location.

To perform accurate calculations, it is essential to take into account factors such as terrain profile, conductor heating temperature, and the level of voltage drop with increasing distance from the power source. The calculations were carried out using the KORTES software environment. The KORTES computer software enables calculation of energy consumption, losses, and traction power system parameters for various train operating modes and schedules [21, 22, 23]. All key data for the section were entered into the program, including the longitudinal track profile with gradients and inclines, curve characteristics, speed limits, stations, and stops. The traction characteristics of the locomotives, as well as the train mass and length, were also taken into account. A sample freight train calculation is shown in Fig. 2, and for a passenger train in Fig. 3.

FIGURE 2. Sample freight train calculation

TABLE 2. Direct direction

| Parameter | Type of electric locomotive |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | OZ-Y | OZ-ELR | 3ES5K | 3VL80s | VL60K |
| Current (A) per km:4 9 20 25 30 35 37 41 45 50 54 | 169 204 248 251 140 147 163 140 262 183 281 | 270 253 299 308 315 295 248 245 319 240 307 | 235 380 391 280 292 395 386 320 384 246 385 | 320 297 292 404 341 343 258 317 375 209 351 | 160 255 246 181 233 199 113 181 271 116 214 |
| Maximum power consumption (kW) | 5990 | 7150 | 9071 | 9069 | 5950 |
| Travel energy consumption (kWh) | 1978.5 | 4501,2 | 4785 | 5147.4 | 2158.8 |
| Current collector voltage (V) per km: 20 25 30 35 41 45 50 54 | 24190 23730 24460 24120 23920 21910 22760 21200 | 23890 23240 22660 22380 22470 21140 21850 20510 | 23200 23480 22890 21300 21510 20320 21760 19440 | 23880 22450 22410 21850 21540 20430 22340 19890 | 24200 24340 23480 23490 23340 21790 23890 21990 |

TABLE 3. Reverse direction

| Parameter | Type of electric locomotive |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | OZ-Y | OZ-ELR | 3ES5K | 3VL80s | VL60K |
| Current (A) per km: 55 51 39 32 14 2 | 151 193 185 174 118 145 | 169 275 319 60 196 0 | 329 364 258 298 379 312 | 292 280 351 148 181 280 | 199 203 160 132 115 172 |
| Maximum power consumption (kW) | 4300 | 6940 | 7280 | 6030 | 4540 |
| Travel energy consumption (kWh) | 1007.5 | 1610.7 | 2288.4 | 2310.6 | 1220.6 |
| Current collector voltage (V) per km 55 51 39 32 14 2 | 23040 22530 23410 23980 25380 25890 | 22710 21240 21710 25290 24980 26000 | 20110 19999 22460 22630 24070 25770 | 20650 21160 21340 24270 25060 25790 | 22180 22370 23740 24450 25400 25870 |

FIGURE 3. Sample passenger train calculation

#### Two Locomotives on the Section

Methods for calculating traction power supply system’s vary depending on how the traction load is represented—either deterministically or probabilistically. Deterministic methods are based on the use of an exact train timetable and allow for the analysis of time-dependent parameters of the traction power network, such as feeder currents If(t), traction substation currents ITSS(t), and voltage at the locomotive pantograph Ulp(t).

The input data for such calculations include the results of traction force computations I(L), the power supply scheme of the contact system, and the train schedule L(t). Based on the timetable, it is possible to determine the trains present on a given section at any point in time, and using the functions In(L), their corresponding current loads can be obtained.

One widely used approach within deterministic methods is the method of uniform time slicing of the train schedule. In this method, the timetable is divided into equal time intervals known as the discretization step. For each time slice, an instantaneous load diagram is constructed, showing the current positions of the trains and the respective traction currents. This enables the calculation of network parameters such as:

If=f(t) – feeder current over time;

ΔU=f(t) – voltage drop dynamics, etc.

The instantaneous diagram method provides a means to evaluate the temporal distribution of electrical loads and identify critical operating conditions of the traction power supply system.

The analysis was carried out for various combinations of trains moving in opposite directions, with indications of current and voltage at each pantograph. In some scenarios (especially involving 3ES5K locomotives), a voltage drops down to 17 kV was noted, which does not comply with standards. (See Table IV)

TABLE 4. Combined movement

| Instant value option | The first train |  |  |  | The second train |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Train type (direction) | l, км | I, А | Uт, кВ | Train type (direction) | l, км | I, А | Uт, кВ |
| 1-combination | OZ-Y (direct) | 25 | 251 | 21.7 | VL60K (back) | 51 | 203 | 19.73 |
| 2- combination | VL60K (direct) | 20 | 246 | 22.56 | OZ-Y (back) | 51 | 193 | 20.66 |
| 3- combination | OZ-Y (direct) | 25 | 251 | 20.18 | 3ES5K (back) | 51 | 364 | 17.02 |
| 4- combination | VL60K (direct) | 20 | 246 | 21.9 | 3VL80s (back) | 55 | 292 | 19 |
| 5- combination | OZ-ELR (direct) | 25 | 308 | 21.25 | VL60K (back) | 51 | 203 | 19.33 |
| 6- combination | 3ES5K (direct) | 20 | 391 | 21.41 | OZ-Y (back) | 51 | 193 | 19.3 |

### ANALYSIS OF RESULTS

Based on the analysis, the following was established:

- O‘z-Y and VL60k ensure stable voltage operation even during single-train movement on the section.

- When operating O‘Z-ELR, 3ES5k and 3VL80s beyond 45 km, voltage drops to 19 kV are observed, allowing operation at 80% power or, with the permission of the Chairman of JSC “О‘zbekiston temir yо‘llari”, at full power [24, 25, 26].

- Combined train movements require limiting the second train’s locomotive power, especially if located beyond 40 km (voltage may drop below 19 kV).

- Simultaneous movement of three trains is allowed only if all trains move in the reverse direction.

- The maximum electric load from locomotives on the section will not exceed 20 MVA, requiring an appropriate reserve at the traction substation.

### CONCLUSION

The conducted analysis showed that with proper train movement distribution and power limitation at certain points, the Samarkand – Urgut section can be efficiently electrified from the Jambay TSS without the need to construct additional traction substations. Based on the results, a voltage and current distribution diagram was constructed for the projected section (Fig. 4).

FIGURE 4. Diagram of voltage distribution at the pantographs of various electric locomotives during forward movement (left) and current distribution for OZ-Y locomotive at the same kilometers (right)

However, a number of works must be carried out at the existing traction substation "Jambay": in accordance with the technical specifications of the Power Supply Department of JSC "Uzbekiston Temir Yullari", it is necessary to determine the power reserve of the substation’s power transformers, install a new catenary feeder cell to supply the new electrified Samarkand–Urgut railway line, ensure proper connection of this feeder to the flexible busbars of the 27.5 kV switchgear, and also provide for the installation of a catenary sectioning post at the junction point of the new railway line. It is also necessary to develop electrical design documentation, including secondary circuits and relay protection and automation (RPA) systems, for the installation of the new catenary feeder cell at the existing "Jambay" traction substation and for the new sectioning post.

The study confirmed that traction load calculations using a deterministic model and the method of uniform time slicing of the train schedule allow for an accurate assessment of the dynamic parameters of the power supply system, including feeder currents and pantograph voltage. It was found that during the simultaneous operation of high-power locomotives on remote sections, voltage drops below acceptable levels may occur, requiring either power limitation or special permission for operation under such conditions.

The maximum load on the Samarkand–Urgut section does not exceed 20 MVA; at the same time, it should be noted that the Jambay traction substation also supplies a section of the high-speed Tashkent–Samarkand line, which has its own electrical load. However, even taking this additional load into account, the total installed capacity of the two 40 MVA transformers at the substation remains sufficient to ensure reliable power supply for both directions, provided that redundancy and selectivity standards are met.

The obtained calculation data can be used in the development of power supply projects and optimization of traffic schedules on the section, as well as in the design of the 27.5 kV outdoor switchgear bay, selection of secondary circuits, and configuration of relay protection settings.

REFERENCES

- Z. Chuanhong, et al., “Power electronic traction transformer - medium voltage prototype,” IEEE Trans. Ind. Electron. 61, 3257–3268 (2014). https://doi.org/10.1109/TIE.2013.2278960

- J. Wang, et al., “Analysis of power quality issues of electrified railway,” in Proc. 8th Int. Conf. Mechanical and Intelligent Manufacturing Technologies (ICMIMT), 179 (2017). https://doi.org/10.1109/ICMIMT.2017.7917459

- A. T. Langerudy, A. Mariscotti, and M. A. Abolhassani, “Power quality conditioning in railway electrification: A comparative study,” IEEE Trans. Veh. Technol. 66, 6653 (2017).

- S. M. M. Gazafrudi, et al., “Power quality issues in railway electrification: A comprehensive perspective,” IEEE Trans. Ind. Electron. 62, 3081 (2014).

- A. Mariscotti, “Direct measurement of power quality over railway networks with results of a 16.7-Hz network,” IEEE Trans. Instrum. Meas. 60, 1604 (2011).

- J. D. Glover, A. Kusko, and S. M. Peeran, “Train voltage analysis for AC railroad electrification,” IEEE Trans. Ind. Appl. 4, 925 (2008).

- S. De La Torre, et al., “Optimal sizing of energy storage for regenerative braking in electric railway systems,” IEEE Trans. Power Syst. 30, 1492 (2014).

- P.-C. Tan, R. E. Morrison, and D. G. Holmes, “Voltage form factor control and reactive power compensation in a 25-kV electrified railway system using a shunt active filter,” IEEE Trans. Ind. Appl. 39, 575 (2003).

- P.-C. Tan, P. C. Loh, and D. G. Holmes, “A robust multilevel hybrid compensation system for 25-kV electrified railway applications,” IEEE Trans. Power Electron. 19, 1043 (2004).

- L. Zanotto, et al., “Filter design for harmonic reduction in high voltage booster for railway applications,” IEEE Trans. Power Del. 20, 258 (2005).

- L. Fan and Y. Zhen-yu, “Analysis and management research on the impact of Shanghai-Nanjing intercity railway traction load on power grid,” in Proc. China Int. Conf. Elect. Distrib. (CICED), 1 (2010).

- S. Zeliang, X. Shaofeng, and L. Qunzhan, “Single-phase back-to-back converter for active power balancing, reactive power compensation, and harmonic filtering in traction power system,” IEEE Trans. Power Electron. 26, 334 (2011).

- S. Zeliang, X. Shaofeng, and L. Qun-zhan, “Development and implementation of a prototype for co-phase traction power supply system,” in Proc. Asia-Pacific Power Energy Eng. Conf. (APPEEC), 1 (2010).

- G. Khromova, et al., “Calculation of main parameters of two-line helical traction transmission of electric locomotive based on diagnostic parameters,” E3S Web Conf. 474, 01040 (2024).

- G. Khromova, D. Radjibaev, and M. Abduvakhobov, “Calculation of dynamic characteristics of elastic self-aligning gear wheel of the locomotive,” E3S Web Conf. 474, 01040 (2024).

- A. Avdeeva, G. Khromova, and D. Radjibaev, “Two-axle bogie vibration damping system with additional damping elements,” E3S Web Conf. 365, 02003 (2023).

- T. M. Nazirkhonov and D. O. Radjibaev, “Research on the parameters influence of the iron donations traction network of Uzbekistan,” AIP Conf. Proc. 2612, 060017 (2023).

- I. Bayanov, et al., “Influence of misalignment of poles on arcing during current collection,” in Safety in Aviation and Space Technologies, Springer, Cham, 181 (2022).

- Z. Yu, et al., “Measurement and analysis of electrical behaviors of offline discharge between high-speed contact wire and pantograph of locomotive,” IEEE Trans. Instrum. Meas. 72, 1 (2022).

- I. Bayanov, et al., “The electric field of the sliding contact during the interaction of the pantograph and the contact wire,” E3S Web Conf. 264, 04029 (2021).

- B. A. Arzhannikov, et al., “Improvement of basic requirements for the system and devices of traction DC power supply,” Russ. Electr. Eng. 87, 525 (2016).

- A. V. Agunov, A. T. Burkov, and M. A. Ivanov, “Model of the traction and external power supply system joint operation,” J. Phys.: Conf. Ser. 2131, 042093 (2021).

- A. Cherpanov and A. Kutsiy, “Modeling of tractive power supply systems for heavy-tonnage trains operation,” in Proc. Int. Russian Automation Conf. (RusAutoCon), 1 (2018).

- K. K. Abishev, A. Z. Kassenov, and K. B. Assylova, “Design justification of half-track propulsor of traction and transport vehicle,” Lect. Notes Mech. Eng., 434 (2022).

- K. K. Abishev, et al., “Some issues regarding the enhancement of technical and economic performance of electric vehicles,” Lect. Notes Mech. Eng., 682 (2024).

- K. K. Abishev, et al., “Study of the interaction of a transport vehicle with an open road,” Lect. Notes Intell. Transp. Infrastruct., 154 (2020).