**Stabilization of Pressure in a Common Pipeline through Frequency-Based Control of Pumping Units**

Islombek Abdullabekov1,2, a), Saidamirkhon Oripov1,Shukhrat Umarov1, Murakam Mirsaidov1, Ravshan Dusmatov 1, Ubaydullo Boqijonov1

1 Tashkent state technical university named after Islam Karimov, Tashkent, Uzbekistan

*2Termez State University of Engineering and Agrotechnology, Termez, Uzbekistan*

a) Corresponding author: [iabdullabekov@gmail.com](mailto:iabdullabekov@gmail.com)

**Abstract.** Parallel pumping systems are widely used in industrial water supply but remain major consumers of electrical energy. This study investigates energy-efficient control and optimization strategies for pumps operating in parallel on a common pressure pipeline. Intelligent optimization methods, including machine learning–based approaches, are analyzed to minimize energy consumption, stabilize pressure, and reduce losses. The results demonstrate that intelligent control significantly improves system efficiency and operational reliability under varying load conditions.


**INTRODUCTION**

Due to climate change and the adverse consequences of environmental degradation, increasing attention is being paid worldwide to the efficient use of electrical energy. In industrial sectors, particularly in electric drive systems of industrial enterprises, ensuring energy efficiency has become a crucial task. Pumping units represent one of the major energy consumers in these sectors, accounting for approximately 20–30% of total electricity consumption [1]. Therefore, significant potential still exists for energy savings through effective control and optimization of pumping units. Although multi-pump systems operating in parallel on a common pressure pipeline are widely used in practice, their energy efficiency is often not sufficiently considered. This efficiency can be substantially improved through the application of advanced control algorithms and optimisation methods [1][3]. Recent studies have employed intelligent approaches such as the gravitational search algorithm, artificial neural networks, NSGA-II, and machine learning techniques for parallel pumping systems. These methods have been shown to minimise the energy consumption of pumping units, enhance overall efficiency, ensure stable delivery pressure, and reduce entropy generation or energy losses [1–4]. Furthermore, the application of intelligent control and optimisation strategies to pumping units operating in parallel on a common pressure pipeline has demonstrated a significant increase in energy-saving potential [3][4]. In this context, intelligent optimisation and control strategies play a vital role in improving the energy efficiency and operational reliability of parallel pumping systems, necessitating a detailed analysis of the interactions between various control parameters and operating conditions [4].

**EXPERIMENTAL RESEARCH**

The development of a block diagram for the control system of a pumping station operating on a common pressure pipeline is aimed at ensuring the stability of the required water pressure in the pipeline. The water supply schedule of a pumping station connected to a common pressure pipeline is characterised by a variable load, since the volume of water delivered to consumers varies significantly at different times of the day. Under such conditions, maintaining stable water pressure in the common pressure pipeline while controlling the pumping station in energy- and resource-efficient operating modes is currently considered one of the priority tasks. As a solution to this problem, a control approach is proposed in which, under variable water consumption rates, the required water pressure in the common pressure pipeline is maintained by sequentially starting parallel-operating pump units connected to the pipeline. Accordingly, the pumping station control system based on this principle is applied to the water supply system, providing stable pressure regulation while improving the overall energy efficiency and operational reliability of the pumping station.

Figure 1 presents the block diagram of the control system for a pumping station operating on a common pressure pipeline, designed to ensure the stability of the required water pressure in the pipeline. The block diagram illustrates four pump units operating on the common pressure pipeline, along with the electric motors driving them. Each pump unit is connected to the common pressure pipeline via communication pipelines. Each communication pipeline is equipped with a check valve, a pressure shut-off valve, and a pressure sensor. In addition, valve-type shut-off devices are installed on the suction pipelines of each pump unit. A pressure sensor is also installed on the common pressure pipeline. The block diagram of the control system consists of the following elements.



**FIGURE 1.** Block diagram of the control system of a pumping station operating on a common pressure pipeline, designed to ensure the stability of the required water pressure in the pipeline.

VFD – variable frequency drive;

L1 ÷ L2 – reactors providing protection against high commutation currents;

SSSB – start-up sequence selection block;

M1 ÷ M4 – induction motors;

P1 ÷ P4 – pumps;

PSV1 ÷ PSV4 – pressure shut-off valves in the communication pipelines;

PS1 ÷ PS4 – pressure sensors;

SPU – setpoint unit;

CU – control unit;

FS – frequency sensor;

SU1 ÷ SU8 – starting devices;

PSVCB1 ÷ PSVCB4 – control blocks of the pressure shut-off valves;

ICB1 ÷ ICB4 – intermediate comparison blocks;

GCB – global comparison block;

CSU1 ÷ CSU4 – control contacts of the starting devices.

The sequential start-up of the control system for a pumping station operating on a common pressure pipeline, designed to maintain the required water pressure in the pipeline, is carried out as follows. Prior to start-up, all shut-off valves are initially in the closed position. The setpoint value of the required water pressure is entered into the command device. At this stage, the variable frequency drive is connected to the power network through the start-up device and the L1 reactor, which provides protection against high commutation currents. The variable frequency drive adjusts the voltage and frequency values, while the L2 reactor and the start-up sequence selection block (SSSB) prepare pump M1 for operation with the assistance of the start-up device SU1. The power contacts of SU1 connect motor M1 to the output terminals of the variable frequency drive, while the control contacts send a signal to the control block of the pressure shut-off valve PSVCB1. Consequently, M1 drives pump P1, creating water flow in the communication pipeline. When the communication pipeline is filled with water and pressure is established, the pressure sensor PS1 in the communication pipeline transmits a signal via the intermediate comparison block ICB1 to the pressure valve control block PSVCB1. PSVCB1 issues a command to open the pressure shut-off valve PSV1. As a result, the water pumped by P1 is delivered from the common pressure pipeline to consumers. The water pressure generated by pump P1 is measured by the overall pressure sensor PS\_total and transmitted to the global comparison block (GCB). The GCB compares the measured pipeline pressure with the setpoint pressure entered in the command device and, through the control unit (CU), authorizes the variable frequency drive to increase the voltage and frequency up to 50 Hz. If, upon reaching 50 Hz, the pressure in the common pressure pipeline remains below the required setpoint, the GCB sends a signal to the start-up sequence selection block (SSSB). SSSB disconnects M1 from the variable frequency drive network via SU1 and connects it to the power supply network through SU5. Following this procedure, the second and third pump units are started sequentially according to the required water pressure.

The parallel operation of the pump units on the common pressure pipeline, as well as the number of pumps, is used to determine their operational efficiency coefficient, ensuring optimal energy performance of the pumping station.

Operation of a single pump unit (PU) of model D12500-24 in the pressure network (Q = 3.69 m³/s, H = 21.5 m, ηPU = 0.78, T = 3636 h).

Two identical pump units of model D12500-24 operating in a common pressure network (Q = 2.43 m³/s, H = 27.75 m, ηPU = 0.74, T = 48 h).

Two dissimilar pump units operating in a common pressure network (Q₁ = 2.72 m³/s, H₁ = 26.1 m, ηPU₁ = 0.77, T₁ = 36 h; Q₂ = 1.75 m³/s, H₂ = 26.1 m, ηPU₂ = 0.76, T₂ = 36 h).

Operation of a single pump unit of model D6300-27 with a driven electric motor type SD2-85-57-8 in the pressure network (Q = 2.26 m³/s, H = 15.5 m, ηPU = 0.61, T = 5064 h).

The efficiency values of the driven electric motors under the considered operating modes are determined according to the following relation:

***.*** (1)

The weighted average efficiency values of the pumps, ***,*** operating in their respective pressure networks, are calculated as follows:

(2)

(3)

The weighted average efficiency values of the driving electric motors, , of pump units operating in a common pressure network are determined as follows:

(4)

(5)

**RESEARCH RESULTS**

An analysis of the operating parameters of the pump units of models D12500-24 and D6300-27, operating in parallel on the common pressure pipeline, is presented. The results of the study encompass variations in water flow rate (Q), water pressure (H), and efficiency coefficient (η) under different operating conditions.

**TABLE 1.** Investigation of the pump units of models D12500-24 and D6300-27 operating in parallel on the common pressure pipeline.

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Number of simultaneously operating pumps of model D12500-24** | **Number of simultaneously operating pumps of model D6300-27** | **Pump of model D12500-24** | | | **Pump of model D6300-27** | | | **,**  **m3/s** |
| **,**  **m3/s** | **,**  **m** |  | **,**  **m3/s** | **,**  **m** |  |
| 1 | - | 3,69 | 21,5 | 0,78 | - | - | - | 3,69 |
| - | 1 | - | - | - | 2,26 | 15,5 | 0,61 | 2,26 |
| 2 | - | 2,43 | 27,75 | 0,74 | - | - | - | 4.86 |
| 1 | 1 | 2,72 | 26,1 | 0,77 | 1,75 | 26,1 | 0,76 | 4,47 |

According to the data in Table 1, when a single D12500-24 pump unit operates in the common pressure pipeline, the water flow rate is 3.69 m³/s, the water pressure is 21.5 m, and the pump efficiency is 0.78. When a single D6300-27 pump unit operates, the water flow rate is 2.26 m³/s, the water pressure is 15.5 m, and the pump efficiency is 0.61. When two D12500-24 pump units operate simultaneously, the water flow rate reaches 4.86 m³/s, the water pressure is 27.75 m, and the pump efficiency is 0.74. When one D12500-24 and one D6300-27 pump unit operate together in the common pressure pipeline, the water flow rate is 4.47 m³/s, the water pressure is 26.1 m, and the pump efficiency is 0.77.



**FIGURE 2.**Q–H characteristics of water flow rate and pressure for the pump units of models D12500-24 and D6300-27 operating in parallel on the common pressure pipeline.

The Q–H characteristics of water flow rate and pressure presented in Figure 2 demonstrate the capability of the pump units operating in parallel on the common pressure pipeline to maintain the required head. These results indicate that the station can provide a stable water supply even under variable load conditions.

**CONCLUSIONS**

The block diagram of the control system for a pumping station operating on a common pressure pipeline ensures stable water pressure in the pipeline by gradually starting multiple pump units operating in parallel on the common pressure pipeline using a single variable frequency drive. The system initiates the pumps at limiting start-up currents without causing hydraulic shocks in the pipeline, thereby maintaining stable pressure in the common pressure network. An automatic control system capable of sustaining the required water pressure in the common pressure pipeline has been developed. The application of this system provides reliable pressure management not only in rural and agricultural pumping systems but also in municipal water supply networks, hot water supply, and centralized heating systems.

**REFERENCES**

1. Gong, Xiaobo; Pei, Ji; Wang, Wenjie; Gan, Xingcheng. Energy efficiency optimization analysis and experimental validation of parallel pumping system based on gravitational search algorithm. Journal of Water Process Engineering Article 2025 <https://doi.org/10.1016/j.jwpe.2025.108071>
2. Wang, Wengjie; Wang, Hongyu; Pei, Ji; Chen, Jia; Gan, Xingcheng; Sun, Qin. Artificial intelligence approach for energy and entropy analyses of a double-suction centrifugal pump. [Energy](https://www.scopus.com/pages/publications/105002390859?origin=resultslist)Article 2025 <https://doi.org/10.1016/j.energy.2025.136046>
3. Gan, Xingcheng; Gong, Xiaobo; Pei, Ji; Pavesi, Giorgio; Yuan, Shouqi. Machine Learning Approaches for Enhancing Energy Efficiency and Stability in Parallel Pumping Systems. [Water Resources Management](https://www.scopus.com/pages/publications/105001569175?origin=resultslist)Article2025 <https://doi.org/10.1007/s11269-024-04043-z>
4. Xingcheng Gan, Ji Pei, Giorgio Pavesi, Shouqi Yuan, Wenjie Wang. Application of intelligent methods in energy efficiency enhancement of pump system: A review. Energy Reports, Volume 8, November 2022, <https://doi.org/10.1016/j.egyr.2022.09.016>
5. Islombek Abdullabekov, Murakam Mirsaidov, Shukhrat Umarov, Murot Tulyaganov, Saidamirkhon Oripov. Optimizing energy efficiency in water pumping stations: A case study of the Chilonzor water distribution facility. AIP Conf. Proc. 3331, 030107 (2025) <https://doi.org/10.1063/5.0305780>
6. Shukhrat Umarov, Khushnud Sapaev, Islambek Abdullabekov. The Implicit Formulas of Numerical Integration Digital Models of Nonlinear Transformers. AIP Conf. Proc. 3331, 030105 (2025); <https://doi.org/10.1063/5.0305793>
7. Murot Tulyaganov, Shukhrat Umarov, Islombek Abdullabekov, Shakhnoza Adilova. Optimization of modes of an asynchronous electric drive taken into account thermal transient processes. AIP Conf. Proc. 3331, 030084 (2025) <https://doi.org/10.1063/5.0305786>
8. Makhsud Bobojanov, Furkat Tuychiev, Nuralibek Rashidov, Alim Haqberdiyev, Islombek Abdullabekov. Dynamic simulation of a three-phase induction motor using Matlab Simulink. AIP Conf. Proc. 3331, 040012 (2025) <https://doi.org/10.1063/5.0305750>
9. M M Mirsadov, B KH Fayzullayev, I A Abdullabekov, A S Kupriyanova, D I Kurbanbayeva and U A Boqijonov. The mutual influence of electromagnetic and mechanical processes in dynamic modes of inertial vibrating electric drives. IOP Conf. Series: Materials Science and Engineering 862 (2020) 062081IOP. <https://iopscience.iop.org/article/10.1088/1757-899X/862/6/062081>
10. Islombek Abdullabekov, Murakam Mirsaidov, Furkat Tuychiev, Ravshan Dusmatov. AIP Conf. Proc. 3152, 040007 (2024) <https://doi.org/10.1063/5.0218880>
11. M M Khamudkhanov, I A Abdullabekov, N B Khamudkhanova, R K Dusmatov and B KH Fayzullayev. Controls of the modes of operation of the pumping station with application of frequency-controlled electric drivel. IOP Conf. Series: Materials Science and Engineering 862 (2020) 062048IOP. <https://iopscience.iop.org/article/10.1088/1757-899X/862/6/062048>
12. Murot Tulyaganov. IOP Publishing Journal of Physics: Conference, 2388, **012099**, (2022), <https://doi.org/10.1088/1742-6596/2388/1/012099>
13. Alexandr D. Petrushin, Murot Tulyaganov. Optimal Control of the Switched Reluctance Motor of High-Speed Rail Transport with an On-Board Energy Source. 2024 International Conference on Industrial Engineering, Applications and Manufacturing (ICIEAM). -2024, <https://doi:10.1109/icieam60818.2024.10553741>
14. Tulyaganov, M. Optimization of natural gas combustion in furnace of steam boilers E3s Web of Conferences Open source preview, 2020, 216, 01155, <https://doi:10.1051/e3sconf/202021601155>
15. Liu J.; Chen H.; Wang X.; Gu J.; Shamiyev M.; Pulatov A.O.; Wheeler P.; Torkaman H.; Musolino A.; Gorbounov Y. A Novel Adaptive Force Ripple Suppressing Method for Double-Sided Switched Reluctance Linear Motor. IEEE Transactions on Transportation Electrification, 2025, <https://doi.org/10.1109/tte.2025.3609443>
16. Hao Chen, Yongqiang Liu, Fan Yang, Wang Xing Xing, Zefu Tan, Li Cai, Antonio Musolino, Qian Huang, Yong Qi, Yokub Tairov, Murat Shamiyev. Research on Temperature Rise and Cooling System Optimization Design of Switched Reluctance Machine. July 2025 Protection and Control of Modern Power Systems 10(4):72-88, <https://doi.org/10.23919/PCMP.2024.000092>
17. Mirisaev, A., Pulatov, A., Muminov, K. Improving the Energy Efficiency of Power Supply Systems and Electrical Equipment of Induction Plants of Metallurgical Enterprises. Aip Conference ProceedingsOpen source preview, 2024, 3152(1), 030004 <https://doi.org/10.1063/5.0218879>
18. Mirisaev,A., Pulatov, A., Shamiev, M. The Impact of the Operation of Electric Drives on the Reliability and Energy Efficiency of Power Supply Systems of Industrial Enterprises. Aip Conference ProceedingsOpen source preview, 2024, 3152(1), 030005 <https://doi.org/10.1063/5.0218881>
19. Abidov Kudrat, Gafurova Mexrnoz. The motion of a particle in a single spatial electromagnetic field. AIP Conf. Proc. 3152, 050018, (2024) <https://doi.org/10.1063/5.0219212>
20. Abidov Kudrat, Gafurova Mexrnoz. Energy-Saving Modes of Operation of Pump Unit, Machine Water Lift Systems. AIP Conf. Proc. 3152, 030019, (2024) <https://doi.org/10.1063/5.0218995>
21. Kudrat Abidov. Improving the reliability of the operation of reclamation pumping stations by using self-starting electric motors. E3S Web of Conferences 384, 01055 (2023) Rudenko International Conference “Methodological Problems in Reliability Study of Large Energy Systems” (RSES 2022). <https://doi.org/10.1051/e3sconf/202338401055>
22. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, D.Xalmanov, Y.Shoyimov, D.Khimmataliev. Mathematical Models and Calculation of Elements of Developed Schemes of Contactless Devices. AIP Conference Proceedings, 3331(1), 040043, (2025), <https://doi.org/10.1063/5.0305748>
23. E.Yuldashev, M.Yuldasheva, A.Togayev, J.Abdullayev, R.Karimov. Energy efficiency research of conveyor transport. AIP Conference Proceedings, 3331(1), 040030, (2025), <https://doi.org/10.1063/5.0305742>
24. E.Usmanov, M.Bobojanov, R.Karimov, D.Xalmanov, N.Tairova, S.Torayev. Contactless Switching Devices Using Nonlinear Circuits. AIP Conference Proceedings, 3331(1), 040031, (2025), <https://doi.org/10.1063/5.0305744>
25. Allabergen Bekishev, Nurali Pirmatov, Dilfuza Kurbanbayeva, Najmiddin Kurbanov, Oliyakhon Zaynieva, Obidkhan Yunusov, Utkir Khudoynazarov, Zinatdin Saimbetov.Achievement of maximum power levels at different wind speeds from wind turners with asynchronous double-way feed generator. AIP Conf. Proc. 3331, 030011 (2025).<https://doi.org/10.1063/5.0305765>
26. Pirmatov, N., Bekishev, A.,Kurbanov, N., Saodullaev, A., Saimbetov , Z. Increasing the efficiency and survivability of synchronous machines with biaxial excitation when operating in transient processes. Proceedings of the AIP conference. Volume 3152, Issue 1, June 17, 2024, <https://doi.org/10.1063/5.0218824>
27. N. B. Pirmatov, U. T. Berdiyev, and ofters. E3S Web of Conferences, 401, **03021**, (2023) <https://doi.org/10.1051/e3sconf/202340103021>
28. Jinfu Liu, Hao Chen,Wenju Yan,Ton Duc Do, Murat Shamiev,Yokub Tairov, Miguel Pablo Aguirre. An Adaptive Electromagnetic Force Distribution Method Based on a Double-sided Switched Reluctance Linear Motor, 22nd International Symposium on Power Electronics (Ee), Novi Sad, Serbia, 2023, pp. 1-6, <https://doi.org/10.1109/Ee59906.2023.10346203>
29. Farrukh Akbarov; Rustam Kabulov; Anvar Alimov; Erkin Abduraimov; Dildora Nasirova. Dependence of output parameters of photovoltaic module based on CIGS solar cells on external temperatures. *AIP Conf. Proc.* 3331, 040046 (2025). <https://doi.org/10.1063/5.0305885>
30. Anvar Alimov; Kudrat Abidov; Erkin Abduraimov; Farrukh Akbarov; Humoyun Muminov. Generalized model of nonlinear inductance and its parameters. *AIP Conf. Proc.* 3331, 040035 (2025). <https://doi.org/10.1063/5.0305883>
31. Anvar Alimov, Erkin Abduraimov; Farrukh Akbarov; Dildora Nosirova. Analysis of the Basic Circuit of Ferroresonant Transistor Parametric Dc Voltage Stabilizers with Built - in Functional Converter. *AIP Conf. Proc.* 3152, 050016 (2024). pp. 1-9. <https://doi.org/10.1063/5.0218823>
32. R.Karimov. AIP Conference Proceedings, 2552, **030014**, (2022). <https://doi.org/10.1063/5.0111533>
33. A.A.Pulatov, M.F.Shaimiev, U.M.Mirsaidov. E3S Web of Conferences 390, **06039**, (2023), <https://doi.org/10.1051/e3sconf/202339006039>
34. Nurali Pirmatov, Abdullo Panoev, and ofters. E3S Web of Conferences, 383, **04046** (2023) <https://doi.org/10.1051/e3sconf/202338304046>
35. Ravshan Dusmatov. Proceedings of the 11th International Conference on Applied Innovations in IT. Volume 11, Issue 1, (2023).
36. T.S.Kamalov. Frequency-regulated electric drive of pumping stations of machine irrigation systems. T.: Fan, 2014, 354 p. (in Uzbekistan).
37. Khashimov A.A., Tulyaganov M.M. Optimization of high-inertial automated drive by expanded application of the Newton-Raphson method. Russian Electrical Engineering Open source preview, 2005, 76(1), p. 9–15
38. Khashimov, A.A., Tulyaganov, M.M. Optimal control of dynamic process concerning highly sluggish electric drives. Elektrotekhnika Open source preview, 1993, (12), p. 35–38