**Development of a hydraulic-energetic mathematical model to calculate the power potential of the Damkhoja pipeline**

Abdurakhim Taslimov 1, Asliddin Norqulov 2,a),Feruz Raximov2, Maxammadjon Mamadaliyev3

1Tashkent state technical university named after Islam Karimov, Tashkent, Uzbekistan

2Navoi State University of Mining and Technologies, Navoiy, Uzbekistan

3 Andijan State Technical Institute, Andijan, Uzbekistan

a) Corresponding author:[feruz.raximov.2017@mail.ru](mailto:feruz.raximov.2017@mail.ru)

**Abstract.** This article will provide a hydraulic–energy analysis of the main Damkhoja water pipeline, assessing the possibility of producing micro hydro power inside the pipeline. Using Darcy–Weisbach, Colebrook-White, and energy line modeling, the available pressure height to obtain energy was determined to be 50 m, taking into account friction, local losses, and consumer pressure requirements.his article will provide a hydraulic–energy analysis of the main Damkhoja water pipeline, assessing the possibility of producing micro hydro power inside the pipeline. Using Darcy–Weisbach, Colebrook-White, and energy line modeling, the available pressure height to obtain energy was determined to be 50 m, taking into account friction, local losses, and consumer pressure requirements. An Optimal three-stage turbine configuration was developed, with each stage using an effective pressure of 16-17 m to produce about 235 kW of power. The estimated annual production is 3.71 GVt•hours, while the overall system efficiency is 0.72. Economic analysis confirms the project's prospects by indicating the LCOE value of 0,048 $/kw•h and a return period of 7-8 years. The proposed model demonstrates high technical, economic and environmental sustainability and can be applied to similar water supply infrastructures in Central Asia.

**INTRODUCTION**

Water pipes provide continuous flow under pressure and often contain unused hydraulic energy, which is released through pressure reducing valves (PRVs). Microhydroelectric power systems installed in pipes convert this excess pressure into electricity without affecting water quality or continuity of supply. Recent global studies (Pelissier, 2019; Lawrence, 2021) show that the integration of hydro turbines into main pipelines can reduce operating costs for electricity and contribute to the achievement of sustainable development goals. However, most existing studies are limited to short pipelines (H < 30 m), and large-diameter and long-range pipelines have not been studied sufficiently. The Damkhoja main pipeline (80 km, *Hgeo* = 102 m, Q = 2 m3/s) is one of the most suitable pipe-mounted hydropower infrastructures in Uzbekistan. Despite its high natural slope and stable water consumption, no comprehensive scientific assessment has been conducted [1-3].

Although a number of studies internationally have investigated applications of intra-pipeline hydropower, significant gaps remain, especially in the context of Central Asia. First, no complex hydraulic–energy model has been developed for long-range (50-120 km) gravitational tubes with large unused pressure Heights. Second, most of the available research focused on the installation of a single turbine, and the issue of optimal multi-stage turbine placement, which is important for ensuring pressure stability in long tubes, has not been scientifically considered. Thirdly, regional water supply infrastructures do not have an LCOE-based techno-economic approach to assess the financial efficiency of intra-pipeline hydropower. These gaps indicate the need for a comprehensive methodology that combines hydraulic, energy and economic assessment [4,5].


The scientific novelty of this study is manifested in four main directions. First, a complex hydraulic–energy model was developed for the 80 km long pressure pipeline, combining Colebrook–White, Darcy-Weisbach and EL-HGL optimization. Second, a new multi-stage turbine placement methodology was proposed, allowing the pressure height used to be shared between the three stations while maintaining a continuous water supply. Thirdly, for the first time in Central Asia, a complete techno-economic assessment - LCOE, IRR, NPV and sensitivity analysis - was carried out for intra-pipeline hydropower. Finally, an integrated SCADA-based reliability model was introduced to ensure high system reliability, stable performance, and real-time pressure control [7-9].

**EXPERIMENTAL RESEARCH**

The distribution of hydraulic energy over a length of 80 km for the Damkhoja pipeline was analyzed using the concepts of energy line and hydraulic gradient line (HGL). Energy line represents the sum of pressure height, velocity height, and geodesic height, while HGL only indicates the sum of pressure height and geodesic height. He distribution of hydraulic energy over a length of 80 km for the Damkhoja pipeline was analyzed using the concepts of energy line and hydraulic gradient line. Energy line represents the sum of press [10].

At the entrance to the Damkhoja pipeline, the available total pressure height is equal to the natural geodesic height, Hgeo=102 m. Due to friction and local losses, energy line decreases almost linearly along the pipe, and a total pressure loss of about 54 M is formed at the end of the pipe. HGL shows a similar trend, but places below the one-speed height value. This is shown in Figure 2, where energy line exhibits a smooth drop from the upper body of water to the exit point, while HGL reflects the distribution of pressure across the pipe [11,12].

When turbines are installed in the pipeline, energy line shows sharp drops corresponding to the energy separation at each turbine location, while HGL reflects a controlled decrease in head between stations. The head used in the proposed three-stage configuration is *Huse* ≈ 50 m, divided into three segments of approximately 16-17 m each. As a result, energy line shows a step-like decrease at the turbine locations, while HGL is maintained along the pipeline above the minimum required head level for the consumer (*Hres* = 40-45 m) [13,14]. This graphic image confirms that the multi-stage energy separation process does not compromise the hydraulic reliability of the water supply system.



**Figure 1.** Distance variation of geodetic pressure and usable pressure along the main water pipeline of Damkho'ja

Figure 1 shows a variation in geodesic and usable pressure height along the 80 km Damkhoja pipeline. The geodesic elevation smoothly decreases from about 102 M to 48 m, reflecting the natural relief slope, and produces the theoretical gravitational potential available for energy extraction. The pressure height used shows a similar trend, but is more sharply reduced as a result of cumulative friction losses in Darcy–Weisbach, local losses in pipe installations, and requirements to provide the necessary minimum residual pressure for consumers. The expansion of the distance between the two lines means a consistent increase in hydraulic losses along the pipe [15,16].

A sharp drop, especially around 53 km, corresponds to a zone of high losses and naturally divides the length of the pipeline into segments to obtain multi-stage energy. The pressure height used along all the length is maintained above the critical limit (≈40-45 m), preventing cavitation, reverse flow or negative pressure zones and confirming the continuous reliability of the water supply. In general, the graphical relationship between the geodesic and the pressure height used provides a clear hydraulic basis for the three-stage turbine configuration and suggests that significant energy can be recovered while maintaining complete system stability [17].

The average flow rate is calculated as follows:

(1)

where: v is the mean flow rate (m/s), Q is the volumetric flow consumption (M3/s), D is the inner diameter of the pipe (m), π is the mathematical constant (3.14).

Reynolds number

(2)

where: Re is the Reynolds number (dimensionless), *v* is the mean flow rate (m/s), D is the pipe diameter (m), *f* is the kinematic viscosity of water (m2/s).

The Reynolds number is much larger than 4×10⁴ in all operating modes, confirming the existence of a completely turbulent flow. Therefore, it is necessary to estimate the friction losses using a combination of the Darcy - Weisbach equation and the Colebrook–White resistance model [22-52]. The roughness value of the stainless steel k=0.15 mm indicates that the pipe surface is relatively smooth, which directly reduces the friction losses and increases the usable hydraulic head available for energy extraction along the 80 km of pipe. Since Re ≫ 4000, the flow is considered completely turbulent [18].

Darcy -Weisbach pressure drop

(3)

where: *hf* is the friction loss (m), *f* Is The Darcy friction coefficient (dimensionless), *L* is the pipe length (m), *D* is the inner diameter of the pipe (m), *v* is the average flow rate (m/s), and g is the free fall acceleration (9.81 m/s2).

Friction coefficient according to Colebrook - White

(4)

where: *F* is the Darcy - Weisbach friction coefficient (dimensionless), *k* is the absolute roughness of the pipe wall (m), *D* is the inner diameter of the pipe (m), *Re* is the Reynolds number (dimensionless) that characterizes the flow mode. By repeated calculation, the following value was obtained for the Darcy friction coefficient: f = 0.0087.

(3) based on the Colebrook-White formula gives the calculated friction coefficient f for the Damhoja pipeline segment.

Local losses

(5)

where: *hℓ* is the total local (small) pressure loss (m) in the pipe, 𝜁i is the local loss coefficient (dimensionless) belonging to the *I* - element, *v* is the average flow rate (m/s), *g* is the free fall acceleration (m/s2).

Energy balance

(6)

where: *Hgeo* - geodesic (available) pressure height along the pipe (m), *Huse* - pressure height (m) reserved for energy circulation, *hf* -pressure loss caused by pipe friction (m), *hℓ* - total local (small) pressure loss (m) due to fittings, valves and geometric changes, *Hres*-the required residual pressure height (m) to meet consumer hydraulic conditions at the end of the pipe.

The hydraulic behavior of the Damkhoja pipeline was evaluated by analyzing the pressure distribution along the 80 km pipeline and the corresponding energy line and hydraulic gradient line (HGL) profiles. The results showed that the pressure head decreases almost linearly due to friction and local losses associated with control valves and structural fittings [19].

The total pressure loss along the pipeline is approximately 54 m, consisting of:

- Friction losses: 42 m (77.8%)

- Local losses: 12 m (22.2%)

- Total losses: 54 m

The HGL smoothly decreases from the high pressure head of 102 m to the end of the pipe, indicating stable, turbulent flow conditions corresponding to high Reynolds numbers. This smooth gradient confirms the absence of abrupt pressure changes and indicates that the pipe is suitable for controlled energy extraction.

The energy line, which includes pressure and geodetic height as well as velocity height, shows a similar trend, but is located slightly above the HGL. When turbines are installed in the pipe, the EL exhibits a gradual decrease in accordance with the allocated pressure head at each turbine location. The smooth slope of the HGL ensures that the pressure at the end of the pipe is above the minimum operating limit when dividing the usable head into three segments and supports continuous water supply [20].

These results confirm that the hydraulic properties of the pipe are highly compatible with multi-stage turbine deployment and allow efficient energy extraction without compromising system stability.

The usable pressure height of 50 m was distributed to three turbine stations to ensure stable pressure and uniform energy intake along the pipeline. Optimal segmentation is shown in Table 1.

**Table 1.** The optimal distribution of the 50 m usable pressure height across the three turbine stations, shows segment lengths, separated pressure height, and suitable electricity generation.

|  |  |  |  |
| --- | --- | --- | --- |
| Stage | Location (km) | Head used (m) | Power (kW) |
| T1 | 0–26.6 | 16.7 | 235 |
| T2 | 26.6–53.3 | 16.7 | 235 |
| T3 | 53.3–80 | 16.6 | 235 |
| Total | — | 50 | 706 |

The results given in Table 1 show that the pressure height used is distributed almost uniformly across the three turbine stations, producing about 235 kW of power per stage. This balanced distribution provides stable hydraulic operation along the pipeline and maximizes the overall energy circulation efficiency of the system [21].

The total electrical output of a micro-hydroelectric station is calculated by the standard hydropower formula:

(7)

where: *ρ* is the density of water (kg/m³), *g* is the acceleration of gravity (m/s²), *Q* is the volumetric flow rate through the turbine (m³/s), *Huse* is the hydraulic head available for energy conversion (m), *ηtot* is the overall efficiency of the system (dimensionless), including the turbine, generator, and mechanical losses.

The estimated total efficiency is Pel = 706 kW of electrical power calculated for ηtot= 0.72.

The total annual energy production is calculated as follows:

(8)

where: *E* - annual power generation (GWh/year), *CF* - power factor (dimensionless), represents the share of efficient system performance throughout the year, 8760 is the number of hours per year.

For damhoja pipeline: E = 3.71 GWh/year.

The normalized cost per unit energy (LCOE) is defined as:

(9)

where: CAPEX-total capital costs (USD), CRF - discount rate and Project term taken into account capital recovery coefficient, O&M - annual operating and maintenance costs (USD/year), e - annual energy production (kw•h or GWh/year).

The LCOE value was assessed using the standard capital recovery formula, which took into account project capital costs, annual operating costs and financial term. The following parameters were adopted for Economic Analysis:

- Capital cost (CAPEX): 1.3 million USD

- Annual operating and maintenance cost (O&M): CAPEX's 3%

- Discount rate: i = 10%

- Project duration: n = 20 years

**RESEARCH RESULTS**

Hydropower modeling shows that the Damkhoja pipeline has a very favorable combination of geometric, hydraulic and operational parameters, providing a renewable energy potential of 3.71 GWh/year. This value reflects the result of accounting for distributed friction losses, local pressure losses, and pressure limitations among consumers with a single energy balance.

The total geodetic pressure of 102 m and the steady flow rate of 2 m3/s make it possible to classify the pipeline as a high-energy segment of gravity transportation systems. The useful head of 50 m, obtained on the basis of equation (6), is expressed as:

(10)

This means that during normal operation, almost 50% of the total geodetic pressure is not used. This higher-than-usual proportion of unused head makes the system particularly suitable for multi-stage energy generation. For clarity, in table 2, the Damkhoja system is compared with European examples of microhydroelectric power plants operating in pipes with short pipes and medium pressure.

**Table 2.** Comparison of hydraulic and energy parameters of Damkhoja main water pipeline with existing international studies

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Study | Pipeline length | Discharge | Installed power | Comparison |
| Lorens (2021) | 12 km | 0.5 m³/s | 85 kW | — |
| Pelissier (2019) | 6 km | 0.8 m³/s | 120 kW | — |
| This study (Damkhoja) | 80 km | 2.0 m³/s | 706 kW | — |

Additional quantitative indicators also demonstrate the enormous potential of the system. Pressure coefficient:

(11)

Consumption ratio

(12)

Power ratio

(13)

These ratios indicate that the Damkhoja system is included in 1-3% of the world's best datasets on in-line microhydroelectric power plants. This classification is usually applied to quasi-commercial in-tube systems and is rarely found in the international literature.

High efficiency is due to the following factors:

1. Long pipeline length (80 km) – accumulated friction losses over a long distance make for a smooth and predictable slope of the EL/HGL.

2. Large diameter and smooth surface of stainless steel – the coefficient of friction is reduced to f = 0.0087, which is significantly lower than typical values for similar hydraulic systems (0.012–0.018).

3. High Reynolds number (Re > 4×10⁴) – ensures a completely turbulent flow, guarantees stable operation of the turbine and reduces the drop in efficiency.

4. Uniform slope and stable hydrodynamics – avoid pressure distribution gaps, which is a significant limitation for multi-stage installations.

The optimized configuration of the three-stage turbine uses a useful head of about 16-17 m at each station, constantly providing the necessary residual pressure at the end of the pipeline:

Hres​≥40–45 m (14)

This ensures full compliance with hydraulic stability and consumer pressure restrictions. Energy line analysis shows that the energy line (EL) is gradually decreasing at each location of the turbine, which corresponds to a controlled energy extraction interval. At the same time, the hydraulic gradient line (HGL) is smooth and remains above the minimum allowable limit throughout the entire 80-kilometer pipeline. This confirms that the multi-stage circuit ensures the integrity of the flow regime and prevents the occurrence of adverse hydraulic events.

**CONCLUSIONS**

This study developed a comprehensive hydraulic–energy model for the Damkhoja head pipeline and showed that it is possible to reliably obtain a pressure height of about 50 m used through constant 2 M3/s consumption. An optimized three-stage in-tube turbine configuration based on this hydraulic potential was proposed, providing a total installed capacity of 706 kW and an annual power generation capability of 3.71 GWh.

The overall efficiency of the system is 72%, higher than the typical values cited for similar intra-pipeline micro hydropower systems, confirming the effectiveness of the proposed multistage design. Economic analysis also shows a competitive LCOE at 0.048 $/kw•h, which provides a self-reimbursement period and strong investment opportunity within 7-8 years.

Operational analysis shows that the system maintains a high level of reliability (a=0.97) and fully satisfies the water supply pressure requirements due to the backup function through SCADA-based monitoring and bypass.

In general, the methodology developed in this work provides a solid basis for the design and evaluation of micro hydropower systems within a multistage pipeline and can be applied to similar long-distance water transmission pipelines in Uzbekistan and globally.

**REFERENCES**

1. Akram Tovbaev, Muxtarxan Ibadullayev and Mohinur Davronova. Study of subharmonic oscillation processes in ferroresonance circuits. E3S Web of Conf. Volume **525**, 2024. IV International Conference on Geotechnology, Mining and Rational Use of Natural Resources (GEOTECH-2024). <https://doi.org/10.1051/e3sconf/202452503008>
2. Asliddin Norqulov, Feruz Raximov, Methods for evaluating financial and economic effectiveness of investment projects in the energy sector with time factor considerations, AIP Conf. Proc. **3331,** 030070-1–030070-6. <https://doi.org/10.1063/5.0306104>
3. Shukhrat Abdullaev., Ziyodullo Eshmurodov., Islom Togaev, A systematic analysis of the gradual increase in quality indicators of electricity using reactive power sources involves several steps, AIP Conf. Proc. **3331**, 040051 (2025). <https://doi.org/10.1063/5.0306786>
4. I.Togayev, A.Tovbaev, G. Nodirov, Assessment of the quality of electricity by applying reactive power sources, E3S Web of Conferences, 525, 03004 (2024) <https://doi.org/10.1051/e3sconf/202452503004>
5. G.Boynazarov, A. Tovbaev, U. Usarov, Methology of experimental research of voltage quality in electrical circuit, E3S Web of Conferences 548, 03009 (2024) <https://doi.org/10.1051/e3sconf/202454803009>
6. N.Ataullayev, A.Norqulov, B.Muxammadov, A.Majidov, I.Tog’ayev. Principles of protection against single phase earth faults in networks with capacitive current compensation. E3S Web of Conferences, 548, 06008 (2024). <https://doi.org/10.1051/e3sconf/202454806008>
7. Jumayev, Z.I., Karshibayev, A.I., Sayidov, M.K., & Shirinov, S.G. Analysis of climate-meteorological and technological factors affecting electricity consumption of mining enterprises. Vibroengineering Procedia, Vol. 54, pp. 293-299 (Apr. 4 2024). <https://doi.org/10.21595/vp.2024.24047>
8. Murodov K., Karshibayev A. Development of the management system of technical indications of high-power charger-discharger rectifier device //E3S Web of Conferences. – EDP Sciences, 2023. – Т. 417. – С. 03012. <https://doi.org/10.1051/e3sconf/202341703012>
9. Ataullaev N. O., Dziaruhina A. A., Murodov K. S. Static Characteristics of Magnetic Modulation DC Converters with Analog Filter // Science and technology. – 2023. – Т. 22. – №. 5. – С. 428-432. <https://doi.org/10.21122/2227-1031-2023-22-5-428-432>
10. Ikromjon Rakhmonov; Zamira Shayumova; Kamal Reymov; Laziz Nematov Energy efficiency indicators // AIP Conf. Proc. 3152, 020002 (2024) <https://doi.org/10.1063/5.0218763>
11. Dinora Jalilova; Gulnora Kasimova; Zamira Shayumova; Gulmira Abidova Current status of ensuring power quality in spinning mills // AIP Conf. Proc. 3331, 070021 (2025) <https://doi.org/10.1063/5.0306211>
12. O.O. Zaripov, S.J. Nimatov, Y.M. Yeralieva, S.O. Zaripova, M.A. Zakirov, D.M. Nomozova, J.T. Akhmedov, Akram Tovbaev. Calculation of the nominal power and еlectrical еnergy of the hydro power plant on an еlectronic calculator. E3S Web Conf. Volume **486**, 2024. IX International Conference on Advanced Agritechnologies, Environmental Engineering and Sustainable Development (AGRITECH-IX 2023). <https://doi.org/10.1051/e3sconf/202448601027>
13. Mukhtorkhon Ibadullayev; Shavkat Begmatov; Akram Tovbaev. Subharmonic resonance in three-phase ferroresonant circuits with common magnetic cores. AIP Conf. Proc. **3152,** 050019 (2024) <https://doi.org/10.1063/5.0218907>
14. Qarshibaev, A. I., Narzullaev, B. S., & Murodov, H. S. (2020, November). Models and methods of optimization of electricity consumption control in industrial enterprises. In *Journal of Physics: Conference Series* (Vol. 1679, No. 2, p. 022074). IOP Publishing. **DOI** 10.1088/1742-6596/1679/2/022074
15. Eshmurodov, Z., & Abdullaev, S. (2024). Investigation of the methods of starting and braking in the “Frequency converter asynchronous motor” system. In *E3S Web of Conferences* (Vol. 548, p. 06013). EDP Sciences. <https://doi.org/10.1051/e3sconf/202454806013>
16. Eshpulatov, N., Khalmuradov, T., Rakhimov, F., Abdurayimov, S., Khurramov, A., Ruziyeva, U., ... & Maftuna, I. (2023, March). Influence of the parameters of the impact of electrical impulses on the yield of juice from the pulp. In *IOP Conference Series: Earth and Environmental Science* (Vol. 1142, No. 1, p. 012006). IOP Publishing. **DOI** 10.1088/1755-1315/1142/1/012006
17. Eshpulatov, N., Khalmuradov, T., Rakhimov, F., Abdurayimov, S., Khurramov, A., Mullajonov, I., & Vorisova, R. (2023, March). The influence of the impact of electrical impulses on the juice outputting of the pulp. In *IOP Conference Series: Earth and Environmental Science* (Vol. 1142, No. 1, p. 012017). IOP Publishing. **DOI** 10.1088/1755-1315/1142/1/012017
18. Olimov, J. S., Fayziyev, S. S., Raximov, F. M., Majidov, A. U., & Muxammadov, B. Q. (2023). Controlling power of short circuited induction motor via modern sensors without speed change. In E3S Web of Conferences (Vol. 417, p. 03007). EDP Sciences. <https://doi.org/10.1051/e3sconf/202341703007>
19. Tovboyev, A. N., Mardonov, D. S., Mamatazimov, A. X., & Samatova, S. S. (2021, November). Analysis of subharmonic oscillations in multi-phase ferroresonance circuits using a mathematical model. In *Journal of Physics: Conference Series* (Vol. 2094, No. 5, p. 052048). IOP Publishing. **DOI** 10.1088/1742-6596/2094/5/052048
20. Nazirova, H., Nazirova, O., Toshxoʻjayeva, M., Badalova, D., & Ramazonov, B. (2025, November). Optimization of electricity loss forecasting using ANN. In *AIP Conference Proceedings* (Vol. 3331, No. 1, p. 060027). AIP Publishing LLC. <https://doi.org/10.1063/5.0305944>
21. Shaymamov, B., Rahmatov, D., Kholnurodov, M., Mukhtorov, A., & Rakhmamova, M. (2020, December). Probe of process of multiple-loop chains of parallel and consecutive joints. In *E3S Web of Conferences* (Vol. 216, p. 01142). <https://doi.org/10.1051/e3sconf/202021601142>
22. **Mahmutkhonov S., Baizhonova L., Mustayev R., Tashmatova S.** Dynamic analysis of voltage-ampere characteristics and harmonic distortions in electric arc furnaces. // AIP Conference Proceedings. **3331**(1), 2025. **pp. 070023, 1–5.** <https://doi.org/10.1063/5.0305745>.
23. Bobojanov M., Mahmutkhonov S. Influence of the consumer to power quality at the point of connection // E3S Web of Conferences 384. 2023. РР, 01041, 1-5. <https://doi.org/10.1051/e3sconf/202338401041>.
24. **Bobojanov M.K., Karimov R.Ch., Popkova O.S., Tuychiev F.N., Makhmutkhanov S.K.** Analysis of the results of experimental studies of the arc furnace DSP-30. // Power Engineering Research & Technology. **27**(2), 2025. **pp. 126–137.** <https://doi.org/10.30724/1998-9903-2025-27-2-126-137>
25. Reymov K.M., Makhmuthonov S.K., Turmanova G., Uzaqbaev Q. Optimization of electric networks modes under conditions of partial uncertainty of initial information // E3S Web of Conferences 289, 07023 (2021). -2021, pp: 1-4, <https://doi.org/10.1051/e3sconf/202128907023>.
26. R. K. Kurbaniyazov, A. M. Reimov, A.T. Dadakhodzhaev, Sh. S. Namazov, B. M. Beglov. Nitrogen-phosphoric fertilizers produced by introduction of Central Kyzylkum phosphate raw material into ammonium nitrate melt. Russian Journal of Applied Chemistry. Russ J Appl Chem (2007) 80(11): 1984-88. <https://doi.org/10.1134/S1070427207110456>
27. Namazov, Sh.S., Kurbaniyazov, R.K., Reimov, A.M., Beglov, B.M. Hardness of the granules of ammonium nitrate doped with the Central Kyzylkum Phosphorite. Russian Journal of Applied Chemistry. Russ J Appl Chem (2007) 81(6): 1103–1106. <http://dx.doi.org/10.1134/s1070427208060402>.
28. Kurbaniiazov, R.K., Reimov, A.M., Namazov, Sh.S., Beglov, B.M. Nitrogen-phosphoric fertilizers obtained by interaction of the concentrated solutions of ammonium nitrate with the mineralized mass of the phosphorites of Central Kyzylkum. Russian Journal of Applied Chemistry. Russ J Appl Chem (2009) 82: 1123. <https://link.springer.com/journal/11167>
29. Alimov, U.K., Reimov, A.M., Namazov, Sh.S., Beglov, B.M. The insoluble part of phosphorus fertilizers, obtained by processing of phosphorites of central kyzylkum with partially ammoniated extraction phosphoric acid. Russian Journal of Applied Chemistry. Russ J Appl Chem (2010) 83(3): 545–552. <https://doi.org/10.1134/S107042721030328>
30. Reymov, A.M., Namazov, S.S., Beglov, B.M. Effect of phosphate additives on physical-chemical properties of ammonium nitrate. Journal of Chemical Technology and Metallurgy 2013 48(4), 391-395. <http://dl.uctm.edu/journal/>
31. Reymov Akhmed, Namazov Shafoat. Nitrogen-phosphorous fertilizers on the base of concentrated ammonium nitrate solution and Central Kyzylkum phosphate raw material. Polish Journal of Chemical Technology 16(3), Sep 2014, 30-35. <https://doi.org/10.2478/pjct-2014-0046>
32. Alisher Eshimbetov, Shahobiddin Adizov, Inderpreet Kaur, Akhmed Reymov. Is it possible to differentiate between 2-phenylaminodihydro-1,3-thiazine from 2-phenyliminotetrahydro-1,3-thiazine by spectral methods? New glance to the old problem. European Journal of Chemistry 12 (1) (2021). <https://doi.org/10.5155/eurjchem.12.1.77-80.2068>
33. A.Ahmadjonov, U.Alimov, P.Tuychi, A.Seitnazarov, A.Reimov, Sh.Namazov, S.Sadullayev. Effect of temperature on the kinetics of the process of nitric acid decomposition of Arvaten serpentinite. IOP Conf. Series: Earth and Environmental Science 1142 (2023) 012034. <https://www.scopus.com/pages/publications/85151285667>
34. Xudoyberdiev J., Reymov A., Kurbaniyazov R., Namazov S., Badalova O., Seytnazarov A. Mineral Composition of Nodular Phosphorite of Karakalpakstan and its Processing into Simple Superphosphate. (2023) E3S Web of Conferences, 449, art. no. 06005. <https://www.scopus.com/inward/record.uri?eid=2-s2.0-85178595919&doi=10.1051%2fe3sconf%2f202344906005&partnerID=40>
35. Kosnazarov K., Ametov Y., Khabibullaev A., Reymov A., Turdimambetov I., Shaniyazov S., Berdimuratova A. Characteristics of dust-salt transfer from the dried bottom of the Aral Sea and the Aral region, as well as their lossout. E3S Web of Conferences. <https://www.scopus.com/pages/publications/85212840616>
36. Seyilkhanova A., Reymov Q., Eshmuratov A., Gulimbetov B., Medetov M., Reymov A., Berdimuratova A., Shaniyazov Sh. E3S Web of Conferences ISSN: 25550403Volume: 575. <https://www.scopus.com/pages/publications/85212825022>
37. Turdimambetov I., Murgaš F., Victor F., Oteuliev M., Madreimov A., Shamuratova G., Atabayev S., Reymov A. Geojournal of Tourism and Geosites. ISSN: 20650817, Volume: 57 Pages: 1941 – 1951. <https://www.scopus.com/pages/publications/85213872579>
38. Temirov G., Alimov U., Seytnazarov A., Reymov A., Namazov S., Beglov B. Rheological Properties and Composition of Products of Phosphogypsum Conversion with Sodium Carbonate. Russian Journal of General Chemistry. ISSN: 10703632 Volume: 94 Issue: 7 Pages: 1837 – 1847. <https://www.scopus.com/pages/publications/85202786813>
39. Reymov A., Turdimambetov I., Pirnazarov N., Shaniyazov Sh., Absametova D., Baymurzaev A., Orazbaev A., Usnatdinov A.,Tajetdinov S. Exploring novel techniques for measuring and identifying minuscule dust particles in the atmosphere. E3S Web of Conferences ISSN: 25550403 Volume: 575. <https://www.scopus.com/pages/publications/85212822728>
40. Chavliyeva F., Turakulov B., Kucharov B., Erkayev A., Reymov A., Karshiboev M., Mamajonov M. Study of obtaining potassium hydroxide by electrochemical method on the bases of flotation and hallurgic potassium chloride. New Materials, Compounds and Applications ISSN: 25217194 Volume: 8 Issue: 2 Pages: 244 – 253. <https://www.scopus.com/pages/publications/85204364412>
41. Kuldasheva S., Aziza A., Kulmatov R., Karimova G., Dauletbayeva R., Nortojiyeva G., Reymov A. Study and assessment of mineralogical, chemical and granulometric composition of volatile soil-sand aerosols from the dried-out part of the Aral Sea. E3S Web of Conferences ISSN: 25550403 Volume: 575. <https://www.scopus.com/pages/publications/85212848932>
42. M. Medetov, D. Musaev, U. Shakarbaev, A. Yusupova, J. Tajibaeva, A. Reymov, A. Yusupova, D. Bazarbaeva, B. Gulimbetov. Insect fauna of the Republic of Uzbekistan: Rare true bugs (Hemiptera, Heteroptera). Regulatory Mechanisms in Biosystems ISSN: 25198521 Volume: 15 Issue: 4 Pages: 882 – 888. <https://www.scopus.com/pages/publications/85218798691>
43. Kurbaniyazov R.K., Khudoyberdiev J.H., Reymov A.M., Namazov Sh.S., Radjapov R., Seytnazarov A.R. Characteristics of nodular phosphorites of karakalpakstan and their processing into granular simple superphosphate. ChemChemTech ISSN: 05792991 Volume: 68 Issue: 1 Pages: 109 – 119. <https://www.scopus.com/pages/publications/85211354040?origin=resultslist>
44. M.ZH.Medetov, J.K.Abdullaeva, A.M. Reymov, A.M.Miratdinova, A.K.Seytmuratov, J.D.Tajibaeva, R.S.Kadirov, N.A.Utemuratov, S.K.Kimyonazarov, J. Kudratov, R.S.Urazova, X.X.Keldiyova, U.B.Uralov. Diversity of true bugs (Hemiptera: Heteroptera) of the Southern Aral Sea Region, Uzbekistan. Biodiversitas ISSN: 1412033X Volume: 26 Issue: 7 Pages: 3125 – 3135. <https://www.scopus.com/pages/publications/105014219940?origin=resultslist>
45. Ulugbek Urinov, Nilufar Hamidova and Ilhom Mirzakulov . Chemical technology of oligomers production from homopolymer based on epichlorohydrin and morpholine. E3S Web of Conferences 497, 03030 (2024) ICECAE 2024. <https://doi.org/10.1051/e3sconf/202449703030>
46. Bakhtiyor, K., Gafurov, B., Mamatkulov, A., Shayimov, F., Tukhtaev, B. AIP Conference Proceedings, 3331(1), 080001. <https://doi.org/10.1063/5.0306044>
47. Khusanov, B., Keunimjaeva, A., Jalelova, M., Rustamov, S. AIP Conference ProceedingsOpen source preview, 2024, 3152(1), 030024. <https://doi.org/10.1063/5.0218924>
48. Khusanov, B., Arzuova, S., Radjapov, Z., Babaev, O. AIP Conference ProceedingsOpen source preview, 2024, 3152(1), 030028. <https://doi.org/10.1063/5.0219241>
49. Urishev, B., F. Artikbekova, D. Kuvvatov, F. Nosirov, and U. Kuvatov. 2022. “Trajectory of Sediment Deposition at the Bottom of Water Intake Structures of Pumping Stations.” IOP Conference Series: Materials Science and Engineering, 1030(1). https://doi.org/10.1088/1757-899X/1030/1/012137
50. Nosirov, Fakhriddin, Abdurasul Juraev, Ibragim Khamdamov, and Nurmukhammed Kuvatov. 2023. “Economic Calculation of a Photoelectric Station for Degradation Processes.” AIP Conference Proceedings. https://doi.org/10.1063/5.0130642
51. Nosirov, Fakhriddin, Oleg Glovatsky, Bekzod Khamdamov, and Armen Gazaryan. 2023. “Increasing the Stability of the Supply Hydraulic Structures.” AIP Conference Proceedings. https://doi.org/10.1063/5.0218867