**Improving the energy efficiency of pump station electric drives through optimal intelligent control**

Elmurod Yuldashev1, a), Islombek Abdullabekov2, Raxmatillo Karimov1, 2,

Elbek Ganiyev1, Iroda Husanova1, Diyorjon Nuritdinov1

1 Almalyk State Technical Institute, Almalyk, Uzbekistan

2 Tashkent state technical university named after Islam Karimov, Tashkent, Uzbekistan

*a) Corresponding author:* [*rahmatillo05.03.1982@gmail.com*](mailto:rahmatillo05.03.1982@gmail.com)

**Abstract.** This paper is devoted to developing an integrated functional architecture for controlling electric drives in pump stations under energy-saving and stable operating modes, and to substantiating its technical effectiveness. The proposed scheme combines, within a single control loop, flexible adjustment of motor speed in accordance with process demands using a frequency converter, limitation of reactive power flow and improvement of the power factor through a capacitor bank, as well as continuous diagnosis of power-quality parameters based on a phase meter. Coordinated control of valves and actuating mechanisms is implemented via the AUMA module, while local control units independently perform the protection and signaling functions of each subsystem, ensuring the modular reliability of the overall system. Based on real-time data, the central control computer carries out monitoring, operating-mode selection, and optimization tasks, helping maintain the pump unit’s operating point near the optimal region. As a result, conditions are created for reducing hydraulic, volumetric, cavitation, electrical, and transient losses, decreasing network loading, and extending equipment service life. The proposed approach is characterized as a practical solution aimed at improving the energy efficiency of dewatering and process pumping systems in mining and industrial environments.

**INTRODUCTION**

Dewatering of deep underground horizons, maintaining dry drifts and stopes, and conveying water for technological processes are critical prerequisites for the uninterrupted operation of the mining industry. In deep mines, water inflow is typically non-stationary: it varies over time due to seasonal and hydrogeological factors, changes in fracture permeability, and the progressive development of mining works. At the same time, the depth and productivity of boreholes and sumps are often heterogeneous, while long-distance pipelines experience continuously evolving hydraulic resistance caused by scaling, corrosion, sediment deposition, and changes in flow regime. Under such complex and dynamic conditions, pumping stations become one of the dominant consumers of electrical power in a mining enterprise [1-3].

Available industrial evidence indicates that pumping systems may account for a significant share of mine electricity consumption, in some cases reaching several tens of percent of total power demand. This high energy burden is intensified by the widespread use of conventional control strategies in which pump units operate at constant speed regardless of actual process requirements. When demand fluctuates and head or flow requirements decrease, fixed-speed operation leads to a systematic mismatch between the supplied hydraulic energy and the required technological load. Consequently, throttling losses increase, the operating point deviates from the best efficiency region, and the overall specific energy consumption rises. In practice, this inefficiency can translate into an additional 20–30% energy use beyond the real-time necessity, particularly in networks where flow regulation is performed by valves rather than speed control [4-9].

These challenges make the transition to intelligent, adaptive pump control not only desirable but strategically necessary for modern mining. Optimal control based on real-time monitoring of inflow, pressure, and energy indicators enables the pump operating point to be continuously aligned with the evolving hydraulic demand. Such approaches can reduce hydraulic and transient losses, mitigate cavitation risk during unstable inflow periods, and lower mechanical stress on equipment. Moreover, the integration of variable frequency drives with power-factor correction and diagnostic modules provides a pathway to improving both the electrical and hydraulic performance of the station as an integrated system. Therefore, the development of intelligent, optimization-based control frameworks for deep-mine pumping infrastructure represents a high-impact engineering direction aimed at reducing energy costs, enhancing operational reliability, and extending the service life of critical dewatering assets [10-16].

**EXPERIMENTAL RESEARCH**

The energy efficiency of pump units is determined by their internal hydraulic, mechanical, volumetric, and electrical losses. The largest share of losses is observed in hydraulic processes: flow separation in the impeller region, increased turbulence, and friction in pipelines cause part of the pressure to be converted into heat. Internal geometric mismatches and deviations of the flow direction further intensify this process. Mechanical losses are associated with friction in bearings, gland seals, and around the shaft, which increases the torque required from the motor. Volumetric losses, in turn, reduce the pump’s actual delivery due to backflow and leakage. A critical drop in pressure leads to cavitation, accelerating impeller wear. Electrical losses arise from the motor’s thermal and magnetic characteristics. Frequent speed changes also cause additional energy consumption in dynamic (transient) regimes. The combined effect of these factors typically limits the overall pump efficiency to the range of 55-75%. Figure 1 presents a loss diagram of the pump system [17-23].

**FIGURE 1.** Distribution of losses in the pump system

Linear variation of a pump’s rotational speed has a direct impact on the hydraulic, mechanical, and energy performance of the system. When the speed is reduced, the flow rate decreases proportionally, while the head decreases in proportion to the square of the speed. As a result, power consumption drops sharply according to the cubic law, leading to a significant improvement in energy efficiency. The reduction in flow velocity also decreases friction losses in the pipeline network and contributes to the stabilization of hydraulic processes. Speed optimization affects volumetric losses as well: because the pressure differential is reduced, backflow decreases and the pump’s actual delivery increases. Mechanical losses are reduced due to lower loading of bearings and seals, which extends the service life of the unit. A decrease in rotational speed also reduces the probability of cavitation, since suction-side pressure variations become less pronounced and critical conditions at the impeller inlet are less likely to occur. The mathematical expressions describing the reduction of losses achieved through linear motor-speed control are presented below in Eqs. (1), (2), and (3) [24-30].

(1)


(2)

(3)

Linear control of the motor speed also leads to the optimization of electrical energy consumption. Thermal and magnetic losses in the rotor–stator pair decrease, thereby improving the overall efficiency of the motor. The smooth nature of the control process eliminates excessive energy use during transient regimes, which enhances the overall stability of the system. In general, linear pump-speed control significantly reduces hydraulic losses, optimally decreases mechanical and volumetric losses, and improves system performance by lowering electrical energy consumption. For this reason, adaptive speed control is considered one of the most effective energy-saving strategies in modern pump stations [31-36].

**RESEARCH RESULTS**

Linear control of the motor speed also leads to the optimization of electrical energy consumption. Thermal and magnetic losses in the rotor-stator pair are reduced, thereby improving the overall efficiency of the motor. The smooth nature of the control process eliminates excessive energy use during transient regimes, which enhances the overall stability of the system. In general, linear control of pump speed significantly reduces hydraulic losses, optimally decreases mechanical and volumetric losses, and improves system performance by lowering electrical energy consumption. Therefore, adaptive speed control is considered one of the most effective energy-saving strategies in modern pump stations [37-41].



**FIGURE 2.** Functional control scheme of the pump unit

This text shows the logical outcome of the proposed control scheme. Since the frequency converter adjusts the motor speed to match the load, the pump operating point shifts closer to the optimal region, leading to lower hydraulic, volumetric, and cavitation losses. The capacitor bank improves the power factor and helps reduce network current and electrical losses. The phase meter and the central control computer monitor power-quality indicators, limiting excessive heating and unstable operating conditions caused by phase unbalance and deviations in operating mode. Fig.3 presents the energy efficiency of the pump system under the baseline mode and under the proposed control scheme [42-45].

**FIGURE 3.** Energy efficiency of the pump system in the baseline mode and under the proposed control scheme

The unit and local control blocks synchronize the control of valves and actuating mechanisms, thereby reducing extra losses that typically arise during transient regimes. In general, the diagram indicates that after implementing the new scheme, the main share of losses remains within the hydraulic group, while electrical and dynamic losses represent a relatively smaller fraction. Therefore, the next optimization stage with the greatest additional benefit may involve reducing hydraulic resistance in the pipeline network, bringing the operating point closer to the BEP, and improving suction conditions. Figure 4 presents the loss diagram of the pump system [46-48].

**FIGURE 4.** Distribution of losses in the pump system

**CONCLUSION**

Achieving energy and resource savings was made possible by intelligent control of the pump unit speed. Experimental results show that hydraulic losses were reduced by 7%, internal hydraulic losses by 1%, mechanical losses by 1%, volumetric losses by 1%, and electrical losses by 1%. As a result, the overall efficiency of the pump unit increased from 60% to 71% (an improvement of 11 percentage points).

**REFERENCES**

1. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, D.Xalmanov, Y.Shoyimov, D.Khimmataliev. *Mathematical Models and Calculation of Elements of Developed Schemes of Contactless Devices*. AIP Conference Proceedings, 3331(1), **040043**, (2025), <https://doi.org/10.1063/5.0305748>

2. E.Yuldashev, M.Yuldasheva, A.Togayev, J.Abdullayev, R.Karimov. *Energy efficiency research of conveyor transport*. AIP Conference Proceedings, 3331(1), **040030**, (2025), <https://doi.org/10.1063/5.0305742>

3. E.Abduraimov. *Automatic control of reactive power compensation using a solid state voltage relays*. Journal of Physics Conference Series, 2373(7), **072009**, (2022). DOI 10.1088/1742-6596/2373/7/072009

4. E.Abduraimov, D.Khalmanov. *Invention of a contactless voltage relay with an adjustable reset ratio*. Journal of Physics Conference Series, 2373(7), **072010**, (2022). DOI 10.1088/1742-6596/2373/7/072010

5. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. *Review of Literature Sources and Internet Materials on Contactless Devices for Reactive Power Compensation*. AIP Conference Proceedings, 3331(1), **040041**, (2025), <https://doi.org/10.1063/5.0305878>

6. M.Sadullaev, M.Bobojanov, R.Karimov, D.Xushvaktov, Y.Shoyimov, H.Achilov. *Experimental Studies of Contactless Devices for Controlling the Power of Capacitor Batteries*. AIP Conference Proceedings, 3331(1), **040044**, (2025), <https://doi.org/10.1063/5.0307195>

7. E.Usmanov, M.Bobojanov, R.Karimov, D.Xalmanov, N.Tairova, S.Torayev. *Contactless Switching Devices Using Nonlinear Circuits*. AIP Conference Proceedings, 3331(1), **040031**, (2025), <https://doi.org/10.1063/5.0305744>

8. K.Abidov, E.Abduraimov, M.Gafurova. *Possibility of Applying Methods of Analysis and Synthesis of Linear Electrical Circuits to Some Nonlinear Circuits*. AIP Conference Proceedings, 3331(1), **040034**, (2025), <https://doi.org/10.1063/5.0305757>

9. K.Abidov, A.Alimov, M.Gafurova. *Transients in Devices of Control Systems With Excitation Winding*. AIP Conference Proceedings, 3331(1), **040033**, (2025), <https://doi.org/10.1063/5.0305756>

10. O.Ishnazarov, N.Khamudkhanova, K.Kholbutayeva, K.Abidov. *Energy Efficiency Optimization in Irrigation Pump Installations*. AIP Conference Proceedings, 3331(1), **040036**, (2025), <https://doi.org/10.1063/5.0305844>

11. K.Abidov, A.Alimov, N.Khamudkhanova, M.Gafurova. *Determination of the Permissible Number of Pumping Units Supplied From the Transformer of the Amu-Zang-I Substation, Selection of the Power of Static Capacitors*. AIP Conference Proceedings, 3331(1), **040029**, (2025), <https://doi.org/10.1063/5.0305754>

12. F.Akbarov, R.Kabulov, A.Alimov, E.Abduraimov, D.Nasirova. *Dependence of Output Parameters of Photovoltaic Module Based on CIGS Solar Cells on External Temperatures*. AIP Conference Parameters, 3331(1), **040046**, (2025), <https://doi.org/10.1063/5.0305885>

13. A.Alimov, K.Abidov, E.Abduraimov, F.Akbarov, H.Muminov. *Generalized Model of Nonlinear Inductance and its.* AIP Conference *Parameters*, 3331(1), **040035**, (2025), <https://doi.org/10.1063/5.0305883>

14. E.Abduraimov, M.Peysenov, N.Tairova. *Development of Contactless Device for Maintaining the Rated Voltage of Power Supply Systems*. AIP Conference Proceedings, 2552, **040012**, (2022). <https://doi.org/10.1063/5.0116235>

15. A.Nuraliyev, I.Jalolov, M.Peysenov, A.Adxamov, S.Rismukhamedov, R.Karimov. *Improving and Increasing the Efficiency of the Industrial Gas Waste Cleaning Electrical Filter Device*. AIP Conference Proceedings, 3331(1), **040040**, (2025), <https://doi.org/10.1063/5.0305751>

16. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. *Development of Contactless Device Schemes for Automatic Control of the Power of a Capacitor Battery*. AIP Conference Proceedings, 3331(1), **040042**, (2025), <https://doi.org/10.1063/5.0305879>

17. E.Abduraimov, D.Khalmanov, B.Nurmatov, M.Peysenov, N.Toirova. *Analysis of dynamic circuits of contactless switching devices*. Journal of Physics Conference Series, 2094(2), **022072**, (2021). DOI 10.1088/1742-6596/2094/2/022072

18. Y.Adilov, A.Nuraliyev, M.Abdullayev, S.Matkarimov. *Dynamic Performance Model of a Hybrid Power System*. AIP Conference Proceedings, 3331(1), **040038**, (2025). <https://doi.org/10.1063/5.0305909>

19. Y.Adilov, M.Khabibullaev. *Application of fiber-optic measuring current transformer in control and relay protection systems of belt conveyor drives*. IOP Conference Series Earth and Environmental Science, 614(1), **012022**, (2020), doi:10.1088/1755-1315/614/1/012022

20. R.Yusupaliyev, N.Musashayxova, A.Kuchkarov. Methods of Purification of Polluted Water from Ammonia Compounds at Nitrogen Fertilizer Plants. E3S Web of Conferences, 563, **03085**, (2024). <https://doi.org/10.1051/e3sconf/202456303085>

21. R.Yusupaliev, N.Kurbanova, M.Azimova, N.Musashaikhova, A.Kuchkarov. Establishing a Water-chemical Regime and Increasing the Efficiency of Combustion of a Mixture of Fuel Oil and Gas in a DE 25-14 GM Boiler: A Case Study of the Kokand Distillery. AIP Conference Proceedings, 2552, **030026**, (2022), <https://doi.org/10.1063/5.0130471>

22. R.Yusupaliev, B.Yunusov, M.Azimova. The composition of natural waters of some source rivers of the republic of Uzbekistan, used in the thermal power engineering and the results of the experimental researches at preliminary and ion exchange treatment of water. E3S Web of Conferences, 139, **01083**, (2019), <https://doi.org/10.1051/e3sconf/201913901083>

23. S.Kasimov, A.Sulliev, A.Eshkabilov. *Optimising Pulse Combustion Systems for Enhanced Efficiency and Sustainability in Thermal Power Engineering*. E3S Web of Conferences, 449, **06006**, (2023), <https://doi.org/10.1051/e3sconf/202344906006>

24. M.Azimova, N.Kurbanova, D.Rakhmatov. Large-scale environmental benefits of biogas technology. AIP Conference Proceedings, 3152(1), **060007**, (2024), <https://doi.org/10.1063/5.0218937>

25. M.Jalilov, M.Azimova, A.Jalilova. On a new technology of preparation of hot drinking water. Energetika Proceedings of Cis Higher Education Institutions and Power Engineering Associations, **60(5)**, (2017), pp.484-492. <https://doi.org/10.21122/1029-7448-2017-60-5-484-492>

26. S.Amirov, A.Sulliev, U.Mukhtorov. *Resonance sensors of motion parameters*. AIP Conference Proceedings, 3256(1), 050028, (2025). <https://doi.org/10.1063/5.0267548>

27. K.Turdibekov, A.Sulliev, O.Iskandarova, J.Boboqulov. *Experimental and statistical methods for studying the modes of electric power systems under conditions of uncertainty*. E3S Web of Conferences, 452, **04002**, (2023), <https://doi.org/10.1051/e3sconf/202345204002>

28. S.Amirov, A.Sulliev, S.Sharapov. *Study on differential transformer displacement sensors*. E3S Web of Conferences, 434, **02011**, (2023), <https://doi.org/10.1051/e3sconf/202343402011>

29. M.Mirsadov, B.Fayzullayev, I.Abdullabekov, A.Kupriyanova, D.Kurbanbayeva, U.Boqijonov. *The mutual influence of electromagnetic and mechanical processes in dynamic modes of inertial vibrating electric drives*. IOP Conference Series Materials Science and Engineering, 862(6), **062081**, (2020). doi:10.1088/1757-899X/862/6/062081

30. S.Amirov, A.Sulliev, K.Turdibekov. *Investigation of biparametric resonance sensors with distributed parameters*. E3S Web of Conferences, 377, **01002**, (2023), <https://doi.org/10.1051/e3sconf/202337701002>

31. M.Yakubov, A.Sulliev, A.Sanbetova. *Modern methods of evaluation of metrological indicators of channels for measurement and processing of diagnostic values of traction power supply*. IOP Conference Series Earth and Environmental Science, 1142(1), **012010**, (2023), doi:10.1088/1755-1315/1142/1/012010

32. K.Turdibekov, A.Sulliev, I.Qurbanov. *Voltage Symmetration in High Speed Transport Power Supply Systems*. AIP Conference Proceedings, 2432, **030084**, (2022), <https://doi.org/10.1063/5.0089958>

33. K.Turdibekov, M.Yakubov, A.Sulliev, A.Sanbetova. *Mathematical Models of Asymmetric Modes in High-Speed Traffic*. Lecture Notes in Networks and Systems, **247**, (2022), pp.1051-1058. DOI:10.1007/978-3-030-80946-1\_95

34. S.K.Shah, L.Safarov, A.Sanbetova, and etc. *Investigation on composite phase change materials for energy-saving buildings*. E3S Web of Conferences, 563, **01003**, (2024), <https://doi.org/10.1051/e3sconf/202456301003>

35. A.Sanbetova, A.Mukhammadiev, A.Rakhmatov, Z.Beknazarova. *Study on cultivation of environmentally friendly seed potatoes based on electrical technology*. E3S Web of Conferences, 377, **03001**, (2023), <https://doi.org/10.1051/e3sconf/202337703001>

36. J.Safarov, A.Khujakulov, Sh.Sultanova, U.Khujakulov. S.Verma. *Research on energy efficient kinetics of drying raw material*. E3S Web of Conferences, 216, **01093**, (2020). <https://doi.org/10.1051/e3sconf/202021601093>

37. J.Safarov, Sh.Sultanova, G.Dadayev, Sh.Zulponov. *Influence of the structure of coolant flows on the temperature profile by phases in a water heating dryer*. IOP Conf. Series: Materials Science and Engineering, 1029(1), **012019**, (2021). doi:10.1088/1757-899X/1029/1/012019

38. Sh.Sultanova, A.Artikov, Z.Masharipova, A.Tarawade, J.Safarov. *Results of experiments conducted in a helio water heating convective drying plant*. IOP Conf. Series: Earth and Environmental Science, 868(1), **012045**, (2021). doi:10.1088/1755-1315/868/1/012045

39. Sh.Sultanova, J.Safarov, A.Usenov, D.Samandarov, T.Azimov. *Ultrasonic extraction and determination of flavonoids*. AIP Conference Proceedings, 2507, **050005**, (2023). <https://doi.org/10.1063/5.0110524>

40. Sh.Sultanova, J.Safarov, A.Usenov, T.Raxmanova. *Definitions of useful energy and temperature at the outlet of solar collectors*. E3S Web of Conferences, 216, **01094**, (2020). <https://doi.org/10.1051/e3sconf/202021601094>

41. Dj.Saparov, S.Sultonova, E.Guven, D.Samandarov, A.Rakhimov. *Theoretical study of characteristics and mathematical model of convective drying of foods*. E3S Web of Conferences, 461, **01057**, (2023). <https://doi.org/10.1051/e3sconf/202346101057>

42. Sh.Zulpanov, D.Samandarov, G.Dadayev, S.Sultonova, J.Safarov. *Research of the influence of mulberry silkworm cocoon structure on drying kinetics*. IOP Conf. Series: Earth and Environmental Science, 1076, **012059**, (2022). doi:10.1088/1755-1315/1076/1/012059

43. A.Tarawade, D.Samandarov, T.Azimov, Sh.Sultanova, J.Safarov. *Theoretical and experimental study of the drying process of mulberry fruits by infrared radiation*. IOP Conf. Series: Earth and Environmental Science, 1112, **012098**, (2022). doi:10.1088/1755-1315/1112/1/012098

44. Sh.Umarov, Kh.Sapaev, I.Abdullabekov. *The Implicit Formulas of Numerical Integration Digital Models of Nonlinear Transformers*. AIP Conference Proceedings, 3331, **030105**, (2025), <https://doi.org/10.1063/5.0305793>

45. I.Abdullabekov, M.Mirsaidov, F.Tuychiev, R.Dusmatov. *Frequency converter – asynchronous motor – pump pressure piping system mechanical specifications*. AIP Conference Proceedings, 3152, **040007** (2024). <https://doi.org/10.1063/5.0218880>

46. I.Abdullabekov, M.Mirsaidov, Sh.Umarov, M.Tulyaganov, S.Oripov. *Optimizing energy efficiency in water pumping stations: A case study of the Chilonzor water distribution facility*. AIP Conference Proceedings, 3331, **030107**, (2025). <https://doi.org/10.1063/5.0305780>

47. M.Bobojanov, F.Tuychiev, N.Rashidov, A.Haqberdiyev, I.Abdullabekov. *Dynamic simulation of a three-phase induction motor using Matlab Simulink*. AIP Conference Proceedings, 3331, **040012**, (2025). <https://doi.org/10.1063/5.0305750>

48. M.Tulyaganov, Sh.Umarov, I.Abdullabekov, Sh.Adilova. *Optimization of modes of an asynchronous electric drive taken into account thermal transient processes*. AIP Conference Proceedings, 3331, **030084**, (2025). <https://doi.org/10.1063/5.0305786>