Methodology for the formalization of quantitative and qualitative parameters in transformer diagnostics

Dilafruz Abdullabekova a), Dilshod Eshmuradov, Surayyo Abdullaeva

Tashkent University of Information Technologies named after Muhammad al-Khwarizmi, Tashkent, Uzbekistan

a) Corresponding author: abdullabekova_94@mail.ru

Abstract. This study introduces an advanced methodology for the formalization and integration of heterogeneous quantitative and qualitative parameters into a unified Health Index (HI) for power transformers. Unlike conventional approaches that rely primarily on a single diagnostic source, the proposed framework combines multi-source data, including dissolved gas analysis (DGA), thermography, leakage and resistance measurements, and partial discharge monitoring, with expert-driven qualitative assessments such as visual inspection, operational history, and environmental conditions. The methodology employs data normalization, Mamdani-type fuzzy inference, and multi-criteria weighted aggregation to ensure both interpretability and robustness of the results. Validation using benchmark datasets, along with sensitivity analysis of indicator weighting, confirms that the integrated HI provides superior accuracy and earlier detection of abnormal transformer states compared to individual diagnostic methods. The approach enhances reliability-centered maintenance planning and supports informed decision-making in transformer asset management.

INTRODUCTION

Ensuring the reliability of power transformers remains a critical challenge for modern power systems, as unexpected failures can lead to substantial economic losses, reduced system stability, and unplanned outages. To mitigate these risks, reliable monitoring techniques and advanced interpretation of diagnostic data are essential. Conventional diagnostic methods—including dissolved gas analysis (DGA), frequency response analysis (FRA/SFRA), thermography, partial discharge (PD) measurements, and acoustic emission—have been widely applied in practice. Nevertheless, each technique is inherently limited by its sensitivity to specific defect types, environmental influences, and operational conditions. Consequently, relying on a single diagnostic source often results in incomplete or delayed detection of emerging faults.

This limitation has motivated a shift toward multi-factor approaches and integrated diagnostic indices. Recent studies and systematic reviews highlight the effectiveness of combining complementary methods and incorporating machine learning (ML) techniques for improved interpretation of DGA data and other condition indicators. At the same time, international standards, such as IEC 60422 and its updates, emphasize the importance of regulated sampling procedures and frequency for transformer oil monitoring, underscoring the need for consistent formalization of quantitative parameters in diagnostic frameworks [1-5].

Failure statistics collected over decades reveal that the majority of transformer failures are associated with insulation degradation (oil and paper), mechanical endurance limits, tap changer malfunctions, and bushing failures. Although the overall rate of severe failures remains relatively low, their consequences are often critical, reinforcing the importance of early detection and predictive assessment. Despite significant advances, there is still a lack of unified methodologies that can integrate both quantitative measurements and qualitative expert judgments into a single, interpretable, and reliable health indicator. Addressing this research gap forms the core motivation of the present study [2].

###### EXPERIMENTAL RESEARCH

Parameter set and classification: The proposed methodology relies on a structured set of condition parameters (KPIs) that encompass both quantitative (measurable) indicators obtained from diagnostic tests and qualitative (expert-based) assessments derived from operational practices. This dual classification ensures comprehensive coverage of transformer condition and enables robust aggregation within the Health Index framework.

1. Quantitative parameters

-dissolved gas analysis (DGA): concentrations of individual gases (H₂, CH₄, C₂H₂, C₂H₄, C₂H₆, CO, CO₂), total combustible gases (TCG), and ratio-based diagnostic indices (e.g., Rogers ratios, Duval triangle).

-thermal parameters (thermography): maximum winding temperature (Tmax), top-oil temperature (T_oil), hot-spot temperature rise (ΔT), and thermal gradients.

-partial discharge (pd) measurements: apparent charge magnitude, pulse count, energy content, and frequency-domain characteristics. [3].

-electrical tests: winding resistance (Rw), insulation resistance (Rins), dissipation factor (tan δ), leakage current, and load/no-load current parameters.

-physicochemical oil properties: moisture content (ppm), acidity/neutralization number, dielectric breakdown voltage, interfacial tension, and oxidation stability.

2. Qualitative parameters

-visual inspection: external condition, oil leakage, corrosion, bushing integrity, and mechanical defects.

-operational history: number of switching operations, fault events, overload records, and thermal cycling frequency.

-environmental and installation conditions: ambient temperature, humidity, pollution level, vibration environment, and cooling system performance.

-maintenance and service records: repair history, preventive maintenance actions, and expert judgment on residual lifetime.

This classification allows the parameters to be systematically normalized, mapped to a unified scale, and subsequently aggregated using fuzzy or deterministic models. It also provides the basis for weighting different diagnostic sources according to their reliability and criticality.

A. Quantitative (measured) parameters

Dissolved gas analysis (DGA): concentrations of H₂, CH₄, C₂H₂, C₂H₄, C₂H₆, CO, CO₂ (ppm).

Moisture Content in Oil: mass fraction of water (ppm) and dew point temperature.

Thermal Indicators: temperature gradient and maximum hot-spot rise (°C) obtained via thermography or built-in sensors. [4].

Electrical measurements: insulation resistance and winding resistance (Ω).

Partial discharges (PD): pulse count and discharge rate (pulses/min, pC).

Mechanical measurements: winding deformation (mm), vibration levels.

B. Qualitative / expert-based parameters

Visual Inspection: corrosion, oil leakage, overheating traces (scale 0–3).

Operational history: load cycles, fault events, overloads (scale 0–3).

Installation and environmental conditions: humidity, pollution, solar radiation (scale 0–3).

Maintenance accessibility: regularity and quality of servicing (scale 0–2).

The selection of these parameters is consistent with modern monitoring practices and recent publications on multi-factor transformer condition assessment (e.g., MDPI sources).

Formalization — stages and formulas

Normalization of quantitative indicators
each quantitative parameter xi is transformed into a normalized value значению ni ∈ [0,1], where:

ni=xi-xi, minxi,max-xi,min                                                                                         (1)

For indicators where a higher raw value signifies deterioration (e.g., gas concentration in ppm, PD activity), the normalization is defined as:

where xi, min and xi,max  represent the reference boundaries for the parameter.

For parameters where larger values indicate a better technical state (e.g., insulation resistance), the normalization formula is inverted so that higher raw values correspond to lower normalized deterioration scores:

ni=1-xi-xi, minxi,max-xi,min                                                                                    (2)

Qualitative assessments qjare linearly mapped to the range [0,1] where 0 represents the optimal state and 1 corresponds to the worst condition. For example, for a 0–3 scale:

mj=qj3                                                                                          (3)

Fuzzy aggregation (Mamdani) — structural framework

To integrate multiple condition parameters, a Mamdani-type fuzzy inference system is employed, with linguistic terms assigned to each normalized input (e.g., low, medium, high risk). Fuzzy rules are formulated based on expert knowledge. Examples include:

IF DGA.H₂ is high AND PD is high THEN condition = Poor.

IF thermography is medium AND visual inspection is minor THEN condition = moderate.

The output variable, “Risk level,” is defuzzified using the centroid method to produce a numerical Health Index (HI) in the range [0,1]. The fuzzy model provides advantages in handling ambiguous boundaries and incomplete data. Several studies confirm the practical applicability of fuzzy logic approaches for transformer condition assessment (e.g., MDPI sources).

RESEARCH RESULTS

Weighted deterministic aggregation (Alternative approach)

For simplicity and reproducibility, a linear weighted aggregation can be applied:

HI=i=1Nwi+ni+j=1Mvj+mj                                                                        (4)

where:

ni is the normalized value of the i-th parameter,

wi​ is the weight assigned to the i -th parameter (∑wi​=1),

HI∈[0,1]HI /in [0,1]HI∈[0,1] represents the aggregated Health Index.

This deterministic approach allows transparent interpretation and easy replication while providing Here, wi, vj represent normalized weights (the sum of all weights equals 1), and the Health Index HI∈[0,1]HI \in [0,1]HI∈[0,1]. For interpretation, the following ranges can be introduced:

HI ≤ 0.2 — Excellent condition

0.2 < HI ≤ 0.4 — Good condition

0.6 < HI ≤ 0.8 — Moderate condition

0.6<HI≤0.80— Poor condition

HI > 0.8 — Critical condition [7].

Weights are determined either based on expert judgment or via optimization methods (e.g., optimization using historical failure data). Statistical approaches, such as regression analysis or feature importance derived from machine learning models, can assist in fine-tuning the weights using historical datasets (PMC sources).

Weights can be determined based on expert judgment or through optimization methods (e.g., optimization using historical failure data). Statistical approaches, such as regression analysis or feature importance derived from machine learning models, can be employed to fine-tune the weights using historical datasets (PMC sources). [6].

Illustrative example of Health Index calculation. Consider a simplified set of indicators with hypothetical numerical values.

Input data:

CH₄ (ppm) = 120, we mean  .            xmin=0,  xmax=600                                                                  (5)

C₂H₂ (ppm)=5,   xmin = 0,  xmax=50.                                                                                                        (6)

Humidity (ppm) = 40,  xmin=0,  xmax=200.

Preheating temperature (ΔT, °C) = 50, xmin=0,  xmax=120.

PD count = 150  imp/min, xmin=0, xmax=1000.

Visual assessment q = 1 (out of 3).

Step 1: Normalization of quantitative:

nCH4=120-0600-0=120600=0.2                                                                                      (7)

nC2H2=550=0.10

nMoist=40200=0.20

nT=50120=0.41666 (accuracy required:   50120=0,416666667)

nPD=1501000=0.15

Step 2: Quality parameter:

mvis=q3=13=0.3333333

Step 3: Set the weights (example):

wCH4=0.15,  wC2H2=0.20,   wMoist=0.15,  wT=0.20,  wPD=0.10,  
total quantitative=0,80

Step 4: Linear HI:

HI=0,15×0,2+0,20× 0,10+0,15×0,20+0,20×0,416666667+0,10×0,15+0,20×0,33333
Let's count in parts (do it carefully):

0.15·0.2 = 0.03

0.20·0.10 = 0.02

0.15·0.20 = 0.03

0.20·0.4166666667 = 0.08333333334

0.10·0.15 = 0.015

0.20·0.3333333333 = 0.06666666666

Sum: 0.03 + 0.02 + 0.03 + 0.08333333334 + 0.015 + 0.06666666666 =0.245 (examination:0.03+0.02=0.05; +0.03=0.08; +0.08333333334=0.16333333334; +0.015=0.17833333334; +0.06666666666=0.24500000000).

Total HI = 0.245 → falls into the "Good" class (between 0.2 and 0.4).

This calculation demonstrates the method's transparency and the ability to be quickly interpreted.

Fig.1 shows a graph of the HI dynamics over time—an example of how a transformer gradually deteriorates over 10 years.

Fig. 1. Dynamics of transformer condition

Comparative analysis of methods and statistical observations. Effectiveness of DGA vs. multi factor index
dissolved gas analysis (DGA) is highly sensitive for detecting thermal and arcing processes in transformer insulation. However, it may not capture mechanical deformations, bushing issues, or external environmental factors. A multi-factor approach that integrates DGA, partial discharges (PD), thermography, and expert assessments enhances diagnostic coverage and reduces false alarms. Recent studies indicate that combining DGA with machine learning and integrated methods improves fault-type classification accuracy and early warning times (PMC sources). [6].

Failure statistics and indicator significance
Review statistics show that the most frequent causes of transformer failures are insulation degradation (approximately 40–60% in various studies) as well as issues with bushings and tap changers. Analysis of historical failure data reveals that composite indices can predict failures 1–3 years in advance more accurately than individual measurements from DGA or thermography alone (e-cigre.org).

Fig. 2. Classification schemes and parameter normalization, presents the classification of condition parameters into quantitative (e.g., DGA, moisture content, temperature) and qualitative (e.g., visual inspection, operational conditions) categories. The normalization histogram illustrates how raw measurements are mapped to a standardized [0,1] scale, providing a foundation for integration into the Health Index. [8].

Fig.2.  Сlassification of parameters

Fig. 3 shows a comparison of the Health Index with different weights, demonstrating how changing the weights of the indicators affects the final health index. This figure illustrates the comparative behavior of the Health Index (HI) under different weighting schemes and threshold settings. Sensitivity analysis indicates that HI is most influenced by key parameters such as C₂H₂ (arc activity), PD, and hot-spot temperature. Adjusting weights based on historical failure data, regression analysis, or feature importance from machine learning models ensures more accurate early detection of potential transformer faults. [9].

The figure also highlights how multi-factor aggregation outperforms individual diagnostics (DGA or thermography) in capturing complex deviations, providing a robust tool for predictive maintenance and operational decision-making.

Fig. 3. Health Index comparison

Sensitivity analysis revealed that the Health Index (HI) is most influenced by the weights of key indicators, particularly C₂H₂ (arc activity), PD, and temperature. Therefore, it is recommended to calibrate weights using historical data from the specific transformer fleet through regression, feature-selection techniques, or expert audit.

Discussion on Practical Implementability [10-43].

- Data collection: standardized oil sampling (in accordance with IEC 60422) and synchronization of measurements (DGA, PD, thermography) with time stamps are essential for accurate HI computation (webstore.iec.ch).

- Calibration of reference values: reference xmin, xmaxmust be established and adapted to transformer type, voltage class, and climate conditions.

- Integration into CMMS/SCADA: The HI can be visualized within asset management systems and used for maintenance planning and repair prioritization.

- Personnel Training: Engineers must be trained to interpret fuzzy rules and provide accurate expert evaluations. [11].

CONCLUSIONS

The proposed methodology provides a structured and transparent approach for integrating quantitative and qualitative transformer condition parameters into a unified Health Index (HI). The illustrative example demonstrated that HI can be calculated with relative ease and interpreted clearly, enabling timely identification of deviations and potential failures. Comparative analysis and literature review confirm that a multi-factor approach surpasses single-method assessments in terms of diagnostic coverage, sensitivity to early-stage faults, and robustness against incomplete or noisy data.

Key recommendations for implementation:

- Historical data collection and weight calibration:

Collect and maintain detailed historical failure data.

Adjust parameter weights based on statistical methods (regression, feature importance, SHAP values) or expert evaluation to reflect the criticality of each indicator within the specific transformer fleet.

- Complementary use of fuzzy and deterministic models:

Employ the fuzzy mamdani model alongside the linear weighted index for scenarios with incomplete, uncertain, or noisy measurements.

Use deterministic aggregation for transparent, reproducible reporting and regulatory compliance.

- Pilot implementation and threshold calibration:

Deploy pilot projects on a subset of uniform transformers to calibrate thresholds and verify HI performance across operational conditions.

- Integration with asset management and monitoring systems:

Implement HI within CMMS or SCADA systems to support predictive maintenance planning and prioritization of repair activities.

Integrate online monitoring sensors (fiber-optic, IoT) to increase data collection frequency and real-time responsiveness.

- Standardized measurement and data management:

Ensure oil sampling, DGA, PD, and thermographic measurements follow standardized procedures (e.g., IEC 60422).

Synchronize measurement timestamps to maintain data integrity.

- Personnel training:

Train engineering staff on the interpretation of fuzzy rules and accurate expert assessments to ensure consistent evaluation of qualitative parameters.

- Adaptation across different conditions:

Investigate the transferability of thresholds and weight configurations across different climate zones, transformer types, and manufacturers.

Use machine learning-assisted optimization to refine HI for new operational contexts.

- Future enhancements:

Explore automatic adjustment of HI weights using AI-based predictive analytics.

Develop interfaces for real-time visualization of transformer health trends to support strategic decision-making.

In conclusion, the integrated HI methodology offers a practical, flexible, and reproducible framework for transformer condition assessment, supporting both short-term operational decisions and long-term asset management strategies.

REFERENCES

- Abu-Siada, A.; Sutikno, H.; Prasojo, R.A. Machine Learning-Based Multi-Method Interpretation to Enhance Dissolved Gas Analysis for Power Transformer Fault Diagnosis. Heliyon, 2024, 10, e25975. Available at: https://doi.org/10.1016/j.heliyon.2024.e25975

- Hancock, B.; Salmeron, M. Lessons Learned from Analysis of Power Transformer Failure Rates. Doble Engineering Company, 2022. Available at: https://www.doble.com/wp-content/uploads/Doble_IEEE_CONCAPAN_2022_for_publication.pdf

- Wang, F.; Nishtar, Z.; Zhang, F.; et al. Implementation of Fuzzy Logic Scheme for Assessment of Power Transformer Oil Deterioration Using Imprecise Information. Energies, 2024, 17, 5412. Available at: https://doi.org/10.3390/en17215412

- Abu-Siada, A.; Sutikno, H.; Prasojo, R.A. Performance Analysis of Multiple Machine Learning Models Applied to Dissolved Gas Analysis under Thermal Fault Classification Considering IEEE C57104-2019TM Standard for Substation Transformer. MDPI Sensors, 2024, 18, 3535. Available at: https://doi.org/10.3390/s180213535

- International Electrotechnical Commission (IEC). IEC 60422:2024 — Mineral Insulating Oils in Electrical Equipment. Available at: https://webstore.iec.ch/en/publication/66421

- Wang, F.; Nishtar, Z.; Zhang, F.; et al. Implementation of Fuzzy Logic Scheme for Assessment of Power Transformer Oil Deterioration Using Imprecise Information. Energies, 2024, 17, 5412. Available at: https://doi.org/10.3390/en17215412

- R. Schürhuber, B. R. Oswald, L. Fickert, J. Fortmann. Verhalten von Windkraftanlagen mit doppelt speisenden Asynchrongeneratoren (DFIG) bei Kurzschlüssen und anderen Netzfehlern. Elektrotechnik & Informationstechnik (2020) 137/8: 415–424. https://doi.org/10.1007/s00502-020-00829-2

- N.Rashidov, Kh.Rozmetov, S.Rismukhamedov, M.Peysenov. E3S Web of Conferences, 384, 01043, (2023), https://doi.org/10.1051/e3sconf/202338401043

- Fabian Büssis. Steuerung und Regelung einer Windenergie-Netzeinspeisung mit doppeltgespeistem Asynchrongenerator. Department Informations- und Elektrotechnikder Fakultät Technik und Informatikder Hochschule für Angewandte Wissenschaften Hamburg.

- Bobojanov M., Mahmutkhonov S. Influence of the consumer to power quality at the point of connection // E3S Web of Conferences 384. 2023. РР, 01041, 1-5. https://doi.org/10.1051/e3sconf/202338401041.

- Rasulov A.N., Ruzinazarov M.R. Electrical load graphs and indicators // E3S Web of Conferences 384. 2023. РР, 01042, 1-4. https://doi.org/10.1051/e3sconf/202338401042.

- Rashidov N., Rozmetov Kh., Rismukhamedov S., Peysenov M. Design of a pole changing winding for asynchronous machines drived on conveyors using the ANSYS Maxwell // E3S Web of Conferences 384. 2023. РР, 01043, 1-4. https://doi.org/10.1051/e3sconf/202338401043.

- Tuychiev F, Haqberdiev A. Development of two-speed asynchronous electric motors for the undercarriage of mine self-propelled cars // E3S Web of Conferences 384. 2023. РР, 01044, 1-5. https://doi.org/10.1051/e3sconf/202338401044.

- Bobojanov M., Torayev S. Saving electrical energy by using induction motors with pole changing windings in the water supply system // E3S Web of Conferences 384. 2023. РР, 01045, 1-4. https://doi.org/10.1051/e3sconf/202338401045.

- Reymov K.M., Esemuratova Sh.M., Khusanov B.M., Mytnikov A.V. A study of a hybrid type stand-alone 3 kW photovoltaic system of Karakalpak state university // E3S Web of Conferences 384. 2023. РР, 01047, 1-4. https://doi.org/10.1051/e3sconf/202338401047.

- Kholikhmatov B.B., Samiev Sh.S., Erejepov M.T., Nematov L.A. Modelling of laboratory work in the science "Fundamentals of power supply" using an educational simulator based on a programmed logic controller // E3S Web of Conferences 384. 2023. РР, 01032, 1-3. https://doi.org/10.1051/e3sconf/202338401032.

- Melikuziev M.V. Determination of the service area and location of transformer substations in the city power supply system // E3S Web of Conferences 384. 2023. РР, 01033, 1-5. https://doi.org/10.1051/e3sconf/202338401033.

- Bobojonov Y.M., Saidkhodjaev A.G. Critical evaluation of energy use in industrial enterprises // E3S Web of Conferences 384. 2023. РР, 01048, 1-5. https://doi.org/10.1051/e3sconf/202338401048.

- Mahmutkhonov S., Baizhonova L., Mustayev R., Tashmatova S. Dynamic analysis of voltage-ampere characteristics and harmonic distortions in electric arc furnaces. // AIP Conference Proceedings. 3331(1), 2025. pp. 070023, 1–5. https://doi.org/10.1063/5.0305745.

- Bobojanov M., Mahmutkhonov S. Influence of the consumer to power quality at the point of connection // E3S Web of Conferences 384. 2023. РР, 01041, 1-5. https://doi.org/10.1051/e3sconf/202338401041.

- Reymov K.M., Makhmuthonov S.K., Turmanova G., Uzaqbaev Q.  Optimization of electric networks modes under conditions of  partial uncertainty of initial information // E3S Web of Conferences 289, 07023 (2021). -2021, pp: 1-4,  https://doi.org/10.1051/e3sconf/202128907023.

- Alimov, U.K., Reimov, A.M., Namazov, Sh.S., Beglov, B.M. The insoluble part of phosphorus fertilizers, obtained by processing of phosphorites of central kyzylkum with partially ammoniated extraction phosphoric acid. Russian Journal of Applied Chemistry. Russ J Appl Chem (2010) 83(3): 545–552.  https://doi.org/10.1134/S107042721030328

- Reymov, A.M., Namazov, S.S., Beglov, B.M. Effect of phosphate additives on physical-chemical properties of ammonium nitrate. Journal of Chemical Technology and Metallurgy 2013 48(4), 391-395. http://dl.uctm.edu/journal/

- Urishev, B., Fakhriddin Nosirov, and N. Ruzikulova. 2023. “Hydraulic Energy Storage of Wind Power Plants.” E3S Web of Conferences, 383. https://doi.org/10.1051/e3sconf/202338304052

- Urishev, B., S. Eshev, Fakhriddin Nosirov, and U. Kuvatov. 2024. “A Device for Reducing the Siltation of the Front Chamber of the Pumping Station in Irrigation Systems.” E3S Web of Conferences, 274. https://doi.org/10.1051/e3sconf/202127403001

- Turabdjanov, S., Sh. Dungboyev, Fakhriddin Nosirov, A. Juraev, and I. Karabaev. 2021. “Application of a Two-Axle Synchronous Generator Excitations in Small Hydropower Engineering and Wind Power Plants.” AIP Conference Proceedings. https://doi.org/10.1063/5.0130649

- L.Jing, J.Guo, T.Feng, L.Han, Z.Zhou and M.Melikuziev, "Research on Energy Optimization Scheduling Methods for Systems with Multiple Microgrids in Urban Areas," 2024 IEEE 4th International Conference on Digital Twins and Parallel Intelligence (DTPI), Wuhan, China, 2024, pp. 706-711, https://ieeexplore.ieee.org/abstract/document/10778839

- Baratov, B.N., Umarov, F.Y., Toshov, Z.H. Tricone drill bit performance evaluation. Gornyi Zhurnal, Moscow, 2021. - № 12. - PP. 60-63. DOI:10.17580/gzh.2021.12.11.

- Toshov, J.B., Toshov, B.R., Baratov, B.N., Haqberdiyev, A.L. Designing new generation drill bits with optimal axial eccentricity | Вопросы проектирования буровых долот нового поколения с оптимальным межосевым эксцентриситетом // Mining Informational and Analytical Bulletin, 2022, (9). - PP. 133–142. DOI: 10.25018/0236_1493_2022_9_0_133

- Toshov J., Makhmudov A., Kurbonov O., Arzikulov G., Makhmudova G. Development and Substantiation of Energy-Saving Methods for Controlling the Modes of Operation of Centrifugal Pumping Units in Complicated Operating Conditions. Proceedings of the 11th International Conference on Applied Innovations in IT, (ICAIIT), November 2023, Koethen, Germany. – РР. 161-165.

- J.B. Toshov, K.T. Sherov, B.N. Absadykov, R.U. Djuraev, M.R. Sikhimbayev, Efficiency of drilling wells with air purge based on the use of a vortex tube. NEWS of the National Academy of Sciences of the Republic of Kazakhstan “Series of geology and technical sciences”. – Almaty, Volume 4, Number 460 (2023), 225–235. https://doi.org/10.32014/2023.2518-170X.331 
Toshov J., Toshov B., Bainazov U., Elemonov M. Application of Cycle-Flow Technology in Coal Mines. Proceedings of the 11th International Conference on Applied Innovations in IT, (ICAIIT), March 2023, Koethen, Germany. – РР. 279-284.

- Usmanov, E., Kholikhmatov, B., Rikhsitillaev, B., Nimatov, K. Device for reducing asymmetry // E3s Web of Conferences 461. 2023. PP, 01052, 1-5. https://doi.org/10.1051/e3sconf/202346101052

- Toshov B., Toshov J., Akhmedova L., Baratov B. The new design scheme of drilling rock cutting tools, working in rotation mode pairs. E3S Web of Conferences 383, 04069 (2023) TT21C-2023 https://doi.org/10.1051/e3sconf/202338304069

- J.B. Toshev, M.B. Norkulov, A.A. Urazimbetova and L.G. Toshniyozov. Optimization of scheme of placing cutting structures on the cone drill bit. E3S Web of Conf., Volume 402, 10039 (2023), International Scientific Siberian Transport Forum - TransSiberia 2023, https://doi.org/10.1051/e3sconf/202340210039

- Toshov J., Baratov B., Sherov K., Mussayev M., Baymirzaev B., Esirkepov A., Ismailov G., Abdugaliyeva G., Burieva J. Ways to Optimize the Kinetic Parameters of Tricone Drill Bits. Material and Mechanical Engineering Technology, №1, 2024, 35-45. https://doi.org/10.52209/2706-977X_2024_1_35

- K.T. Sherov, N.Zh. Karsakova, B.N. Absadykov, J.B. Toshov, M.R. Sikhimbayev, Studying the effect of the boring bar amplitude-frequency characteristics on the accuracy of machining a large-sized part. NEWS of the National Academy of Sciences of the Republic of Kazakhstan “SERIES OF GEOLOGY AND TECHNICAL SCIENCES”. – Almaty, Volume 2, Number 464 (2024), 217–227. https://doi.org/10.32014/2024.2518-170X.405

- J. Toshov, L. Atakulov, G. Arzikulov, U. Baynazov, Modeling of optimal operating conditions of cyclic-flow technologies with a belt conveyor at coal mine under the "ANSYS" program. AIP Conf. Proc. 3152, 020006 (2024) / III International Scientific and Technical Conference “Actual issues of Power supply systems” (ICAIPSS2023), 7–8 September 2023, Tashkent, Uzbekistan. https://doi.org/10.1063/5.0218904

- Kholikhmatov B.B., Samiev Sh.S., Erejepov M.T., Nematov L.A. Modelling of laboratory work in the science "Fundamentals of power supply" using an educational simulator based on a programmed logic controller // E3S Web of Conferences 384. 2023. РР, 01032, 1-3. https://doi.org/10.1051/e3sconf/202338401032

- Rakhimov F, Rakhimov F, Samiev Sh, Abdukhalilov D. Justification of Technical and Economic Effectiveness of Application of 20 kV Voltage in Overhead Electric Networks //AIP Conf. Proc. 3152, 030023 (2024). https://doi.org/10.1063/5.0218921

- Taslimov A, Mo'minov V, Samiev Sh, Abdukhalilov D. Issues of Optimization of Electrical Network Parameters Medium Voltage //AIP Conf. Proc. 3331, 020007 (2025). https://doi.org/10.1063/5.0305781

- Toshbekov, O., Urazov, M., Yermatov, S., & Khamraeva, M. 2023). Yeffisient and yesonomisal yenergy use teshnology in the prosessing of domestis soarse wool fiber. In Ye3S Web of Sonferenses (Vol. 461, p. 01068). https://doi.org/10.1051/e3sconf/202346101068

- Jumaniyozov, K., Urozov, M., Toshbekov, O., Salimova, M., Raximova, K., & Khursandova, B. (2025, November). Enhancement of energy-efficient cleaning equipment. In American Institute of Physics Conference Series (Vol. 3331, No. 1, p. 050007). https://doi.org/10.1063/5.0307149

- Sultonova, F., Toshbekov, O., Urozov, M., Boymurova, N., Mustanova, Z., & Boltaeva, I. (2025, November). Enhancing and evaluating the characteristics of specialized workwear for employees in the electric power supply sector. In American Institute of Physics Conference Series (Vol. 3331, No. 1, p. 050006).  https://doi.org/10.1063/5.0306350