Analysis of the Installation of the Equivalent Circuit and Vector Diagram of Transverse Compensation in Electrical Networks

Akram Tovbaev 1, Odiljon Zaripov 2,5, Samad Nimatov 2,a), Marjona Olimjonova2, Shahlo Zaripova 3, Sevinch Olimjonova 4

1Navoi State University of Mining and Technologies, Navoi, Uzbekistan

2Tashkent state technical university named after Islam Karimov, Tashkent, Uzbekistan

3Karshi Institute of Engineering Economics, Karshi, Uzbekistan

4National university of Uzbekistan, Tashkent, Uzbekistan

5 Almalyk State Technical Institute, Almalyk, Uzbekistan

a) Corresponding author: Nimatov@mail.ru

Abstract. This article analyzes the cross-compensation substitution scheme of reactive power compensation and the construction of a vector diagram. The main purpose of transverse compensation is to improve the power factor. In such compensation, power losses and voltage reductions have been analyzed for their pre-compensation and postcompensation States by placing capacitors in electrical grids. In addition the vector diagram of the transverse capacitance compensation chain and the vector diagram on the voltages at the beginning and end of the transverse compensatory network have been studied. In this case, the question of determining the C capacitance and reactive power Qkb required to increase the power coefficient from cosφ1 to cosφ2 by exceeding the natural value of the consumer's power coefficient from the vector diagram to transverse compensation has been seen.

INTRODUCTION

In general reactive power compensation is the achievement of increasing the power coefficient. One of the important types of compensation is transverse compensation. In the compensating process, the greatest reduction in power losses in electrical networks is achieved by deploying capacitors. This makes it possible to increase the voltage level that is transmitted along with the placement of capacitors. This process will largely depend on the position where the capacitors are located.

It is known that under the influence of transverse compensation, in addition to the current load of the existing elements in the power supply system, it leads to a decrease in the voltage in the network and the appearance of a voltage ratio at the beginning and end of the power grid [1-2, 21-24, 37-39].

If there is a need for transverse capacitance compensation, this is done using capacitor devices installed in certain areas of the power supply system. To this end, it is necessary to consider alternating current electrical circuits to which electricity consumers and parallel capacitor batteries are connected to calculate and analyze cross-compensation as a reactive power source [3-6, 25-27, 35-36].

LITERATURE SURVEY

In cross-compensation analysis, a circuit is obtained in which the electricity consumer and capacitor batteries are connected in parallel. The network currents in Node a of the usbu Circuit Switching Scheme are found based on the equation in which Kirchhoff's first law is constructed (Fig.1) [7-8, 28-31]. According to him IL tok is defined as follows:

IL=Id+ IKB                                                                            (1)

where IL, Id,  IKB-are the vector values of the currents in the network, charge and capacitor batteries, respectively.

FIGURE 1. Transverse capacitance compensation replacement scheme

In accordance with Kirchhoff's first law (1), the construction of the flow and Vector diagram of the current vectors is shown in Fig.2.

FIGURE 2. Vector diagram of cross-capacitive compensation in a circuit

Transverse compensation, as a vector diagram for a network consisting of a load at the end of the network to which the Xkb capacitor battery is connected. Although this does not take into account the active resistance of the capacitor battery. Since the capacitor battery is connected in parallel with the consumer, the consumer's load current to the φ1-angle φ2- - angle decreases from the I1 value to the I2 value. In this, the amount of current in the network decreases, i.e. ∆I=I1 -I2. In the power supply system, the current is reduced by the same amount in electrical consumers as the existing generators and capacitor generate QKB reactive power from where the batteries are installed. The active and reactive organizers of reactive power waste ∆Pq    and   ∆Qqare reduced due to reduced load on the network and generators. As a result, the total reactive power capacitor battery is reduced to QKB power [7-8, 32-34].

∆P =QKBU2∙R ;              ∆Q =QKBU2∙x                                                               2

here R and X -are the active and reactive resistance of energy system consumers.

The cross-sectional surface of the conductor being selected for the projected network is found as follows.

∆F=∆Ije                 						(3)

where  ∆I- is the decrease in network Current;   Je- is the economic density of network Current.

Accordingly, a voltage drop occurs on the network in accordance with the nominal power reduction of the transformer. As a result, the capacitor connected to the network reduces the voltage drop at the expense of the QKB of power in the battery and is found as follows [15-18, 40-43]:

ΔU=P⋅R+(Q-QKB)⋅XU U.                                                                          (4)

However, when the installed capacity of the capacitor banks significantly exceeds the required level, the reactive current may become larger than the consumer’s inductive current. In such a case, the inequality IBK>IdI holds, leading to overcompensation and a shift of the power factor into the capacitive region. Then the angle φ2 is less than zero and the power factor passes through cosφ=1 and the power is in the quadrant of the capacitance. The result is excessive compensation. Capacitance Current flows from the consumer to the source, and the network Current increases with an increase in IC capacitance current. In this case, the increase in the capacity of C and the dependence on the IL network Current corresponds to the angle φ2 in a certain range, that is, it is recommended to have a limit φ2≥0  and cosφ≤+1. The vector diagram is shown in Fig.2 [18-21, 44-48].

To increase the natural power factor before applying cross-compensation, it will be necessary to increase the cosφ1 power factor at the start of the network to a higher value of the cosφ2 power factor at the end of the network.

In this, the vector allows you to determine the reactive power of the С capacitance and capacitor battery, which will be necessary using the diagram, and the Iс current is found as follows:

IC=IdL1- IdL1=Iatgφ1-Iatgφ2=Iatgφ1-tgφ2                                            (5)

Thus, it follows that Ic=UxKB=UωC and ˕Ia=PU taking into account that UωC=PUtgφ1-tgφ2  thus, we obtain.

Accordingly, the capacitor is the sig and reactive power of the battery,

C=PU2ωtgφ1-tgφ2QKB= U2ωC=Ptgφ1-tgφ2                                                                 (6)

For the purpose of bringing the power factor closer together, the load is used to compensate for the capacitive organizers of the IKB current in inductance connected parallel to the load when it is in a capacitive character [49-51].

This can happen in special cases, when enterprises have long-term high-voltage cable lines in the period when the network load is low, and the entire capacity of capacitors only works during the nominal load hours of enterprises. The voltages at the end of the network can be expressed in two ways on a vector diagram (Fig.3) [52].

FIGURE 3. Vector diagram on voltage values at the beginning and end of a transverse compensable electrical network

The first is when there is no transverse compensation system across the entire network; the second is when there is a possible compensation that increases the power factor to cosφ2=1. Vector diagrams of the voltage U 2 at the end of the power line and the constant voltage values of the active power in the consumer are shown in Figure 3. According to the diagram, the absolute values of the U1 voltage at the beginning of the transmission network and the U 2 voltage at the end of the transmission network, as well as transverse compensation, cause the angle to change from one φ value to 0 values, so it is observed that the voltage from the U1 voltage to the U 2 voltage is small [53.

The scheme for connecting to the loading chain of the capacitor device for the transverse compensation process is shown in Fig. 4.

FIGURE 4. Scheme of connecting capacitance to a transverse compensation loading chain

When a sinusoidal voltage is given to the clamps of the circuit shown in the figure, the power of a single-phase capacitor is determined by the following expression:

Q= U2ωC .                                                                                     (7)

where U- is the grid voltage; C- is the capacitance of the three - phase capacitor.

In general, the capacity of three-phase capacitor batteries to which the Triangle is connected is also determined as above. In this case, the power of a three-phase capacitor in a star circuit, to which it is connected to a network voltage, is determined by the following ratio:

Q= 13U2ωC .                                                                                  (8)

where C- is the sum of the capacities of all phases of a three-phase network.

Given the above designations, the power factor up to compensation is expressed in terms of tgφ1=QP and the power factor after compensation in terms of tgφ2=Q-QKBP. Accordingly, it follows that cosφ2>cosφ1 since tgφ2<tgφ1.

Active power waste in the pre-compensation network

∆P1=3I 2R=S 2U2R=P 2+Q 2U2R                                                              (9)

Active power waste in the post-compensation network

∆P2=P 2+Q-Qkb2U2R                                                                             (10)

Reduction of active power waste after compensation in the network

∆P1-∆P2=P 2+Q 2U 2R-P 2+Q-QKB2U 2R=2Q-QKB∙QKBU 2R.                                       (11)

RESEARCH RESULTS

The apparent power prior to compensation can be expressed as

S1=Pcos⁡φ1

whereas after compensation it is determined by

S2=Pcos⁡φ2,

Accordingly, the ratio of these quantities is obtained as

S1S2=cosφ1cosφ2.             					      (12)

From this relationship, it is evident that when cos⁡φ2>cosφ1, the condition S2<S1 holds. This implies that the apparent power requirement decreases with the improvement of the power factor after compensation. Hence, the apparent power before compensation is inversely related to the improved power factor [7-8, 54-59].

Voltage drops in the system, both before and after compensation, can be represented in the following form:

∆U1=3 ∙I (R cosφ+ X sin φ)

or post-substitution are expressed as:

∆U1 =P∙R+Q∙XU                                                                                 (13)

while the voltage waste after compensation is

∆U2 =P∙R+Q-Qkb∙XU                                                                          (14)

The decrease in the voltage waste per minute, as well as the decrease in voltage at the end of consumers (13) and (14), taking into account the expressions, will be as follows:

∆U1-∆U2=P∙R+Q∙XU-P∙R+Q-Qkb∙XU=Qkb∙XU                                                   (15)

A change in the consumer load leads to a change in voltage in the network. Considering the determination of voltage waste at full load before compensation according to the above expression (13), while at full load the voltage waste is calculated as follows:

∆U’1 =k∙P∙R+Q∙XU                                                                             (16)

where k- is the coefficient proportional to the decrease in load.

Reducing the voltage waste in a state where the network is not at full load is expressed as:

∆U1-∆U’1=P∙R+Q∙XU -k∙P∙R+Q∙XU=(1-k)P∙R+Q∙XU = (1-k)∆U1                                 (17)

At full load, the post-compensation voltage waste, (14) formula is expressed as:

∆U2 =P∙R+Q-Qkb∙XU                                                                    (18)

When not at full load, the

∆U’2 =k∙P∙R+kQ-Qkb∙XU                                                              (19)

Reducing the voltage waste of the network during post-compensation and incomplete loading is equivalent to:

∆U2-∆U’2=P∙R+Q-Qkb∙XU -k∙P∙R+kQ-Qkb∙XU =

=P∙R+Q-Qkb∙X-k∙P∙R+kQ-Qkb∙XU=                                                      (20)

=PR+QX-kPR+QXU =1-kPR+QXU=(1-k)∆U1

It follows from the expression (20) induced above that the oscillation of post-compensation voltages when load decreases in the network is like the oscillation of pre-compensation voltages (17) expression. But the voltage level will be greater. In this case, the decrease in voltage waste (15) is determined according to the expression, since the decrease in voltage waste is due to the change in the constant value Qkbs and Xs for electrical devices [7-8, 60-65].

CONCLUSIONS

Analysis shows that the voltage level in the network during the transverse compensation process can increase to a constant value, depending on the capacity of the installed capacitor bank, the installation location, and the reactance of the connected elements. Transverse compensation is recognized as an effective approach for minimizing active power losses while preserving the magnitude of transmitted power. Alternatively, it facilitates an increase in the transmission capacity of the electrical network without a proportional rise in power dissipation.

Moreover, according to established principles of power system analysis, in addition to the processes of reactive power generation and absorption, capacitive and inductive elements of electrical networks inherently exhibit compensatory interactions. This phenomenon is extensively employed in modern power supply systems to achieve reactive power compensation, which not only enhances the stability of voltage profiles but also contributes to a significant reduction in both voltage drops and total power losses.

REFERENCES

1. M.Ibadullayev, Sh.Begmatov, A.Tovbaev. Subharmonic Resonance in Three-Phase Ferroresonant Circuits with Common Magnetic Cores. AIP Conference Proceedings, 3152(1), 050019, (2024). https://doi.org/10.1063/5.0218907

2. A.Tovbaev, M.Ibadullayev, M.Davronova. Study of subharmonic oscillation processes in ferroresonance circuits. E3S Web of Conferences, 525, 03008, (2024). https://doi.org/10.1051/e3sconf/202452503008

3. O.Jumaev, M.Ismoilov. Filtering errors in primary sensor signals. E3S Web of Conferences, 414, 05008, (2023). https://doi.org/10.1051/e3sconf/202341705008

4. F.Raximov, A.Taslimov, A.Majidov, A.Norqulov. Optimization of losses by switching to higher voltage in distribution networks. E3S Web of Conferences, 525, 03009, (2024). https://doi.org/10.1051/e3sconf/202452503009

5. I.Togayev, A.Tovbaev, G.Nodirov. Assessment of the quality of electricity by applying reactive power sources. E3S Web of Conferences, 525, 03004, (2024). https://doi.org/10.1051/e3sconf/202452503004

6. O.O.Zaripov, S.J.Nimatov, A.N.Tovboev, Y.M.Eralieva, S.O.Zaripova, M.A.Zakirov, D.M.Nomozova, J.T.Akhmedov. Calculation of the nominal power and electrical energy of the hydro power plant on an electronic calculator. E3S Web of Conferences, 486, 01027, (2024). https://doi.org/10.1051/e3sconf/202448601027

7. A.N.Tovboyev, I.B.Togayev, I.Q.Uzoqov, G.Y.Nodirov. Use of reactive power sources in improving the quality of yelectricity. E3S Web of Conferences, 414, 03001, (2023). https://doi.org/10.1051/e3sconf/202341703001

8. G.Boynazarov, A.Tovbaev, U.Usarov. Methology of experimental research of voltage quality in electrical circuit. E3S Web of Conferences, 548, 03009, (2024). https://doi.org/10.1051/e3sconf/202454803009

9. F.Rakhimov. Study of reliability indicators of cable lines in rural areas. E3S Web of Conferences, 525, 03014, (2024). https://doi.org/10.1051/e3sconf/202452503014

10. K.G.Abidov, O.O.Zaripov, N.B.Khamudkhanova, M.U.Idriskhodjaeva, Sh.O.Zaripova. Specific Features of Operating Pumping Units and the Tasks of Ensuring Energy-Saving Modes of Operation by Controlling Them. AIP Conference Proceedings, 2552, 030022, (2022), https://doi.org/10.1063/5.0112384

11. K.G.Abidov, O.O.Zaripov, A.I.Rakhmatullaev, N.O.Zaripov, Sh.O.Zaripova. Calculation methodology for determining the number of simultaneous self-starting pumping units. E3S Web of Conferences, 289, 07003, (2021), https://doi.org/10.1051/e3sconf/202128907003

12. K.G.Abidov, Sh.O.Zaripova, N.B.Khamudkhanova, S.A.Dusmukhamedova, M.O.Gafurova, H.Baratov. Analytical mathematical model of the pumping unit of machine water lifting systems. E3S Web of Conferences, 289, 07004, (2021), https://doi.org/10.1051/e3sconf/202128907004

13. I.A.Abdullabekov, M.M.Mirsaidov, O.O.Zaripov, S.J.Nimatov, Y.M.Eralieva. Reducing reactive energy consumption by optimizing operating modes of irrigation pumping stations. E3S Web of Conferences, 486, 06017, (2024), https://doi.org/10.1051/e3sconf/202448606017

14. S.M.Turabdzhanov, J.M.Tangirov, P.M.Matyakubova, N.S.Amirkhulov, S.S.Khabibullaev. Methods of providing metrological supply when pumping water into wells in oil fields. AIP Conference Proceedings, 3045(1), 030073, (2024), https://doi.org/10.1063/5.0197355

15. M.Makhsudov, O.O.Zaripov, N.Akbarova, Sh.O.Zaripova. Asynchronous in Motors Reactive Power Current for Monitoring and Control Modifiers Scientific, ETC. AIP Conference Proceedings, 3152(1), 050021, (2024), https://doi.org/10.1063/5.0218837

16. M.Mirsadov, B.Fayzullayev, I.Abdullabekov, A.Kupriyanova, D.Kurbanbayeva, U.Boqijonov. The mutual influence of electromagnetic and mechanical processes in dynamic modes of inertial vibrating electric drives. IOP Conference Series Materials Science and Engineering, 862(6), 062081, (2020). doi:10.1088/1757-899X/862/6/062081

17. I.Abdullabekov, M.Mirsaidov, F.Tuychiev, R.Dusmatov. Frequency converter – asynchronous motor – pump pressure piping system mechanical specifications. AIP Conference Proceedings, 3152, 040007 (2024). https://doi.org/10.1063/5.0218880

18. I.Abdullabekov, M.Mirsaidov, Sh.Umarov, M.Tulyaganov, S.Oripov. Optimizing energy efficiency in water pumping stations: A case study of the Chilonzor water distribution facility. AIP Conference Proceedings, 3331, 030107, (2025). https://doi.org/10.1063/5.0305780

19. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, D.Xalmanov, Y.Shoyimov, D.Khimmataliev. Mathematical Models and Calculation of Elements of Developed Schemes of Contactless Devices. AIP Conference Proceedings, 3331(1), 040043, (2025), https://doi.org/10.1063/5.0305748

20. E.Yuldashev, M.Yuldasheva, A.Togayev, J.Abdullayev, R.Karimov. Energy efficiency research of conveyor transport. AIP Conference Proceedings, 3331(1), 040030, (2025), https://doi.org/10.1063/5.0305742

21. A.Nuraliyev, I.Jalolov, M.Peysenov, A.Adxamov, S.Rismukhamedov, R.Karimov. Improving and Increasing the Efficiency of the Industrial Gas Waste Cleaning Electrical Filter Device. AIP Conference Proceedings, 3331(1), 040040, (2025), https://doi.org/10.1063/5.0305751

22. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. Development of Contactless Device Schemes for Automatic Control of the Power of a Capacitor Battery. AIP Conference Proceedings, 3331(1), 040042, (2025), https://doi.org/10.1063/5.0305879

23. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. Review of Literature Sources and Internet Materials on Contactless Devices for Reactive Power Compensation. AIP Conference Proceedings, 3331(1), 040041, (2025), https://doi.org/10.1063/5.0305878

24. K.Abidov, A.Alimov, M.Gafurova. Transients in Devices of Control Systems With Excitation Winding. AIP Conference Proceedings, 3331(1), 040033, (2025), https://doi.org/10.1063/5.0305756

25. A.Alimov, K.Abidov, E.Abduraimov, F.Akbarov, H.Muminov. Generalized Model of Nonlinear Inductance and its. AIP Conference Parameters, 3331(1), 040035, (2025), https://doi.org/10.1063/5.0305883

26. M.Sadullaev, M.Bobojanov, R.Karimov, D.Xushvaktov, Y.Shoyimov, H.Achilov. Experimental Studies of Contactless Devices for Controlling the Power of Capacitor Batteries. AIP Conference Proceedings, 3331(1), 040044, (2025), https://doi.org/10.1063/5.0307195

27. K.Abidov, E.Abduraimov, M.Gafurova. Possibility of Applying Methods of Analysis and Synthesis of Linear Electrical Circuits to Some Nonlinear Circuits. AIP Conference Proceedings, 3331(1), 040034, (2025), https://doi.org/10.1063/5.0305757

28. O.Ishnazarov, N.Khamudkhanova, K.Kholbutayeva, K.Abidov. Energy Efficiency Optimization in Irrigation Pump Installations. AIP Conference Proceedings, 3331(1), 040036, (2025), https://doi.org/10.1063/5.0305844

29. K.Abidov, A.Alimov, N.Khamudkhanova, M.Gafurova. Determination of the Permissible Number of Pumping Units Supplied From the Transformer of the Amu-Zang-I Substation, Selection of the Power of Static Capacitors. AIP Conference Proceedings, 3331(1), 040029, (2025), https://doi.org/10.1063/5.0305754

30. F.Akbarov, R.Kabulov, A.Alimov, E.Abduraimov, D.Nasirova. Dependence of Output Parameters of Photovoltaic Module Based on CIGS Solar Cells on External Temperatures. AIP Conference Parameters, 3331(1), 040046, (2025), https://doi.org/10.1063/5.0305885

31. E.Usmanov, M.Bobojanov, R.Karimov, D.Xalmanov, N.Tairova, S.Torayev. Contactless Switching Devices Using Nonlinear Circuits. AIP Conference Proceedings, 3331(1), 040031, (2025), https://doi.org/10.1063/5.0305744

32. E.Abduraimov, M.Peysenov, N.Tairova. Development of Contactless Device for Maintaining the Rated Voltage of Power Supply Systems. AIP Conference Proceedings, 2552, 040012, (2022). https://doi.org/10.1063/5.0116235

33. E.Abduraimov. Automatic control of reactive power compensation using a solid state voltage relays. Journal of Physics Conference Series, 2373(7), 072009, (2022). DOI 10.1088/1742-6596/2373/7/072009

34. E.Abduraimov, D.Khalmanov. Invention of a contactless voltage relay with an adjustable reset ratio. Journal of Physics Conference Series, 2373(7), 072010, (2022). DOI 10.1088/1742-6596/2373/7/072010

35. E.Abduraimov, D.Khalmanov, B.Nurmatov, M.Peysenov, N.Toirova. Analysis of dynamic circuits of contactless switching devices. Journal of Physics Conference Series, 2094(2), 022072, (2021). DOI 10.1088/1742-6596/2094/2/022072

36. Y.Adilov, A.Nuraliyev, M.Abdullayev, S.Matkarimov. Dynamic Performance Model of a Hybrid Power System. AIP Conference Proceedings, 3331(1), 040038, (2025). https://doi.org/10.1063/5.0305909

37. Y.Adilov, M.Khabibullaev. Application of fiber-optic measuring current transformer in control and relay protection systems of belt conveyor drives. IOP Conference Series Earth and Environmental Science, 614(1), 012022, (2020), doi:10.1088/1755-1315/614/1/012022

38. R.Yusupaliyev, N.Musashayxova, A.Kuchkarov. Methods of Purification of Polluted Water from Ammonia Compounds at Nitrogen Fertilizer Plants. E3S Web of Conferences, 563, 03085, (2024). https://doi.org/10.1051/e3sconf/202456303085

39. R.Yusupaliev, N.Kurbanova, M.Azimova, N.Musashaikhova, A.Kuchkarov. Establishing a Water-chemical Regime and Increasing the Efficiency of Combustion of a Mixture of Fuel Oil and Gas in a DE 25-14 GM Boiler: A Case Study of the Kokand Distillery. AIP Conference Proceedings, 2552, 030026, (2022), https://doi.org/10.1063/5.0130471

40. R.Yusupaliev, B.Yunusov, M.Azimova. The composition of natural waters of some source rivers of the republic of Uzbekistan, used in the thermal power engineering and the results of the experimental researches at preliminary and ion exchange treatment of water. E3S Web of Conferences, 139, 01083, (2019), https://doi.org/10.1051/e3sconf/201913901083

41. P.Matyakubova, P.Ismatullaev, J.Shamuratov. Development of vibration viscometer for industry purpose and experience of its practical. E3S Web of Conferences, 365, 05012, (2023), https://doi.org/10.1051/e3sconf/202336505012

42. M.Azimova, N.Kurbanova, D.Rakhmatov. Large-scale environmental benefits of biogas technology. AIP Conference Proceedings, 3152(1), 060007, (2024), https://doi.org/10.1063/5.0218937

43. M.Jalilov, M.Azimova, A.Jalilova. On a new technology of preparation of hot drinking water. Energetika Proceedings of Cis Higher Education Institutions and Power Engineering Associations, 60(5), (2017), pp.484-492. https://doi.org/10.21122/1029-7448-2017-60-5-484-492

44. K.Turdibekov, A.Sulliev, O.Iskandarova, J.Boboqulov. Experimental and statistical methods for studying the modes of electric power systems under conditions of uncertainty. E3S Web of Conferences, 452, 04002, (2023), https://doi.org/10.1051/e3sconf/202345204002

45. S.Amirov, A.Sulliev, U.Mukhtorov. Resonance sensors of motion parameters. AIP Conference Proceedings, 3256(1), 050028, (2025). https://doi.org/10.1063/5.0267548

46. S.Amirov, A.Sulliev, S.Sharapov. Study on differential transformer displacement sensors. E3S Web of Conferences, 434, 02011, (2023), https://doi.org/10.1051/e3sconf/202343402011

47. S.Kasimov, A.Sulliev, A.Eshkabilov. Optimising Pulse Combustion Systems for Enhanced Efficiency and Sustainability in Thermal Power Engineering. E3S Web of Conferences, 449, 06006, (2023), https://doi.org/10.1051/e3sconf/202344906006

48. S.Amirov, A.Sulliev, K.Turdibekov. Investigation of biparametric resonance sensors with distributed parameters. E3S Web of Conferences, 377, 01002, (2023), https://doi.org/10.1051/e3sconf/202337701002

49. M.Yakubov, A.Sulliev, A.Sanbetova. Modern methods of evaluation of metrological indicators of channels for measurement and processing of diagnostic values of traction power supply. IOP Conference Series Earth and Environmental Science, 1142(1), 012010, (2023), doi:10.1088/1755-1315/1142/1/012010

50. K.Turdibekov, A.Sulliev, I.Qurbanov, S.Samatov, A.Sanbetova. Voltage Symmetration in High Speed Transport Power Supply Systems. AIP Conference Proceedings, 2432, 030084, (2022), https://doi.org/10.1063/5.0089958

51. K.Turdibekov, M.Yakubov, A.Sulliev, A.Sanbetova. Mathematical Models of Asymmetric Modes in High-Speed Traffic. Lecture Notes in Networks and Systems, 247, (2022), pp.1051-1058. DOI:10.1007/978-3-030-80946-1_95

52. S.K.Shah, L.Safarov, A.Sanbetova, and etc. Investigation on composite phase change materials for energy-saving buildings. E3S Web of Conferences, 563, 01003, (2024), https://doi.org/10.1051/e3sconf/202456301003

53. A.Sanbetova, A.Mukhammadiev, A.Rakhmatov, Z.Beknazarova. Study on cultivation of environmentally friendly seed potatoes based on electrical technology. E3S Web of Conferences, 377, 03001, (2023), https://doi.org/10.1051/e3sconf/202337703001

54. G.Boboyev, N.Inatova. The Importance of Implementing Energy Management Systems for Manufacturing Enterprises in the Republic of Uzbekistan. AIP Conference Proceedings, 3331(1), 040047, (2025). https://doi.org/10.1063/5.0305865

55. G.Boboyev, N.Nurmukhamedov, O.Zaripov. Improvement of Means of Measuring the Main Parameters of Electricity. AIP Conference Proceedings, 3331(1), 040039, (2025). https://doi.org/10.1063/5.0305861

56. A.T.Rakhmanov, G.G.Boboev. Developing the Technology for Manufacturing Ohmic Contacts and Sealing Semiconductor Temperature Converters. Journal of Engineering Physics and Thermophysics, 98(3), (2025), pp.841-845. https://doi.org/10.1007/s10891-025-03163-6

57. N.I.Avezova, P.R.Ismatullayev, P.M.Matyakubova, G.G Boboyev. Multifunctional Heat Converter Moisture Content of Liquid Materials. International Conference on Information Science and Communications Technologies Applications Trends and Opportunities Icisct 2019, 9012041, (2019). DOI: 10.1109/ICISCT47635.2019.9012041

58. M.Bobojanov, F.Tuychiev, N.Rashidov, A.Haqberdiyev, I.Abdullabekov. Dynamic simulation of a three-phase induction motor using Matlab Simulink. AIP Conference Proceedings, 3331, 040012, (2025). https://doi.org/10.1063/5.0305750

59. M.Tulyaganov, Sh.Umarov, I.Abdullabekov, Sh.Adilova. Optimization of modes of an asynchronous electric drive taken into account thermal transient processes. AIP Conference Proceedings, 3331, 030084, (2025). https://doi.org/10.1063/5.0305786

60. Sh.Umarov, Kh.Sapaev, I.Abdullabekov. The Implicit Formulas of Numerical Integration Digital Models of Nonlinear Transformers. AIP Conference Proceedings, 3331, 030105, (2025), https://doi.org/10.1063/5.0305793

61. J.Safarov, A.Khujakulov, Sh.Sultanova, U.Khujakulov. S.Verma. Research on energy efficient kinetics of drying raw material. E3S Web of Conferences, 216, 01093, (2020). https://doi.org/10.1051/e3sconf/202021601093

62. J.Safarov, Sh.Sultanova, G.Dadayev, Sh.Zulponov. Influence of the structure of coolant flows on the temperature profile by phases in a water heating dryer. IOP Conf. Series: Materials Science and Engineering, 1029(1), 012019, (2021). doi:10.1088/1757-899X/1029/1/012019

63. Sh.Sultanova, A.Artikov, Z.Masharipova, A.Tarawade, J.Safarov. Results of experiments conducted in a helio water heating convective drying plant. IOP Conf. Series: Earth and Environmental Science, 868(1), 012045, (2021). doi:10.1088/1755-1315/868/1/012045

64. Sh.Sultanova, J.Safarov, A.Usenov, D.Samandarov, T.Azimov. Ultrasonic extraction and determination of flavonoids. AIP Conference Proceedings, 2507, 050005, (2023). https://doi.org/10.1063/5.0110524

65. Dj.Saparov, S.Sultonova, E.Guven, D.Samandarov, A.Rakhimov. Theoretical study of characteristics and mathematical model of convective drying of foods. E3S Web of Conferences, 461, 01057, (2023). https://doi.org/10.1051/e3sconf/202346101057