Methodology for the Calculation and Selection of Elements of Solid-State Thyristor Voltage Relays

Erkin Abduraimov 1,a), Farrukh Akbarov 1, Gulnoz Abdukayimova 1,

Nigora Tairova 1,2, Ibodat Xaldibaeva 1

1Tashkent state technical university named after Islam Karimov, Tashkent, Uzbekistan

2 Almalyk State Technical Institute, Almalyk, Uzbekistan

a) Corresponding author: abduraimoverkin69@gmail.com

Abstract. This paper presents a methodology for the calculation and selection of elements required for the development of compact solid-state thyristor voltage relays. The proposed design integrates a highly sensitive input-voltage monitoring system with high-power actuating components capable of switching large load currents. Based on the analysis of existing literature and the outlined calculation procedure, an example of element selection is provided, including the schematic diagram and experimental characteristics of the developed solid-state voltage relay.

INTRODUCTION

Currently, power supply systems of industrial enterprises predominantly employ contact-based switching devices (contactors, relays, starters, circuit breakers, etc.). However, such devices have several significant drawbacks; including arcing at the moment of switching, low electrical and mechanical durability of contacts, high inertia of the system, and others. Replacing these switching devices with solid-state solutions is therefore a highly relevant task, enabling increased reliability, reduced device dimensions, and improved quality of the supply voltage. The objective of the calculation is to determine the required parameters of the elements in the circuit of the developed solid-state thyristor voltage relay (STVR). In selecting semiconductor components, the following factors are considered: maximum transmitted power, rated current, maximum amplitude of the operating voltage, frequency of current pulses, cooling conditions, maximum reverse voltage, and maximum gate current amplitude. The selection of resistances in the thyristor control circuits is performed with regard to the maximum control current values. The capacitance of the control capacitor is determined based on the power of the thyristor control circuit and the required time constant of the circuit [1-5, 25-27, 34-36].

METHODOLOGY FOR CALCULATION AND SELECTION OF ELEMENTS

The calculation and selection of elements for the STVR should reasonably begin with the power thyristor connected in the diagonal of the diode bridge. The following input parameters must be known: rated load power, supply voltage, and frequency. In the power circuit, a single-phase thyristor AC switch configuration is applied, utilizing a diode bridge with the power thyristor connected in its diagonal. In this scheme, the current in the load flows only when the diagonal of the rectifier bridge is short-circuited by the thyristor, and the reverse voltage across the thyristor is zero, since it is always subjected to voltage of the same polarity. The reverse voltage across the diodes of the bridge is equal to the forward operating voltage of the thyristor and is determined by [6-11, 31-33]:

Urev.=1,41U						(1)

Since the thyristor conducts both half-waves of the current consecutively without interruption, the maximum average current through the thyristor equals 0.9 of the RMS load current. The average current through each diode of the bridge is 0.45 of the RMS load current. In the calculation, it may be assumed that the RMS current through the load is equal to the RMS current through the thyristor [12-13].

The thyristor must have a maximum forward voltage rating that exceeds the peak value of the supply voltage Ufor.max.≥Um (the reverse voltage is zero). The maximum forward average current of the thyristor should satisfy If.max.≥0,637In.rms. and the permissible surge current should not be less than the RMS load current In.rms. In the proposed STVR circuits, the control signal for the power thyristor is applied from the capacitor plates through the resistance Rcon. The capacitor voltage Uс equals the maximum value of the secondary transformer winding voltage, or, in the case of the optocoupler scheme, the maximum value of the mains voltage. The resistance Rcon can be determined by:

Rcon = Uс / I g.thy. 						(2)

where, Ig.thy. - is the RMS value of the thyristor gate current.

The capacitor parameters are selected based on these values. When choosing the capacitance, the capacitor discharge time across Rcon must be taken into account. The capacitor should not discharge completely during one full period of the sinusoidal current, i.e., the discharge time constant should satisfy: > 0,02s. quad =50 Hz.

In the control system, two low-power thyristors connected in series are selected based on the maximum reverse anode-cathode voltage or the capacitor voltage. In this case, the maximum reverse voltage rating of the thyristor must be chosen with an adequate safety margin [14-16, 28-30].

The resistors in the control circuit of the low-power thyristors are selected based on the gate current requirements. The resistor connected in series with the diode determines the switching time or the relay actuation voltage. Therefore, this resistor is preferably a variable resistor, which allows adjusting the relay triggering voltage (to compensate for thyristor parameter tolerances). The diode type in this circuit is selected according to the gate current of the low-power thyristor. The resistance in the gate circuit of the other thyristor is chosen smaller than that of the resistor in series with the diode, since this thyristor must always remain ready for switching the entire device.

For the design of the input low-power transformer in the STVR control circuit, the starting data are the combined power requirements of the control circuit elements [17-24, 46-47].

The calculation of the control transformer should begin with the selection of the magnetic core, i.e., determination of its configuration and geometric dimensions. The most widely used magnetic core designs include laminated shell-type, tape-wound shell-type, and tape-wound toroidal cores. For low-power applications, ranging from a few watts to several tens of watts, shell-type transformers are the most convenient. They feature a single bobbin with windings and are relatively simple to manufacture [25-27, 56].

CALCULATION OF THE CONTROL CIRCUIT TRANSFORMER

For the calculation of the low-power input transformer of the STVR control circuit, the initial data consist of the combined power consumption of the control circuit elements.

The design procedure should begin with the selection of the magnetic core, i.e., determination of its configuration and geometric dimensions. The most widely used magnetic core types include laminated shell-type, tape-wound shell-type, and tape-wound thyroidal cores. For low-power applications, from a few watts up to several tens of watts, shell-type transformers are the most suitable. They employ a single bobbin for winding's and are relatively simple to manufacture [28-36, 49-51].

The initial simplified input data are:

- primary winding voltage U1;

- secondary winding voltage U2;

- secondary winding current I2.

The power of the secondary winding can be determined as:

Sout=I2·U2						(3)

The dimensions of the magnetic core of the chosen construction can be found using the following expression [1]:

(4)

where:

- Scs – cross-sectional area of the magnetic core at the coil position;

- Swa – window area of the magnetic core;

- Bmax – maximum magnetic flux density;

- J – current density;

- Kwf – window filling factor;

- Kst – stacking factor of the magnetic core steel.

The values of electromagnetic loadings В and J depend on the output power of the secondary winding. For shell-type cores with output power Рout=5-15 Wt, the flux density ranges from 1.1 to 1.3 Tl, while the current density ranges from 3.9  to 23.9 A/mm2.

The window filling factor Kwf=0.22-0.29 for windings made of round enamel-coated wire. The stacking factor Kst depends on the thickness of the steel, magnetic core design (laminated or tape-wound), and insulation method of laminations or strips. For the present case, its value lies in the range Kst=0.75-0.89 for steel thicknesses of 0.1-0.2 mm. By determining the product Scs Swa, one can select the required linear dimensions of the magnetic core, ensuring that the obtained ratio is not less than the calculated value. The rated current of the primary winding is determined by [37-42, 53]:

(5)

where the values of η and cosφ of the transformer depend on the transformer power and can be approximately assumed to be η in the range of 0.6-0.7; cosφ in the range of 0.85-0.9 depending on the output power.

The secondary winding current is usually specified. The cross-sectional area of the winding conductor is given by:

(6)

and its diameter by:

(7)

The number of turns in the windings is determined from:

(8)

where:  - winding voltages, - the voltage drop in the windings is within =20÷13; =25÷18 depending on the load capacity 1-4, 43-47.

EXAMPLE OF CALCULATION AND SELECTION OF ELEMENTS

The calculation and selection of the STVR elements were performed in accordance with the proposed methodology and recommendations [48-52].

Initial data:

- Rated load power: Sn=1000VA;

- Supply voltage: Umains=220V;

- Supply frequency: f=50Hz.

Calculation procedure:

- Based on the rated load power and the rated mains voltage, the load current for an active load is determined:

- From the commutated load voltage, the maximum amplitude of the operating voltage applied to the valve is calculated using Eq.(1):

- From the obtained results, a thyristor type VT151-500R is selected, designed for medium-power switching applications [53].

Electrical parameters of thyristor VT151-500R:

- Package: SOT-78;

- Off-state voltage: 500 V;

- Gate trigger current (max.): 15 mA;

- On-state current (max.): 12 A.

- The average current of the diodes forming the bridge is equal to 0.45 of the RMS load current. Since the RMS load current is approximately equal to the RMS thyristor current:

Id = It ·0,45= 2,043 А

When selecting the diode type, it must be ensured that the bridge diodes protect the circuit from reverse voltage during negative half-cycles of the anode voltage. The maximum permissible reverse voltage of these diodes must satisfy:

Where Um is the mains voltage amplitude. Based on the calculation results, diodes type D246B are selected, with Urev=400V and Id=5 A [2, 54].

- The maximum capacitor voltage:

Uс =2U2 =1,4124  31 V,

where U2=24V is the voltage of the transformer secondary winding.

- The resistance R3 limiting the gate current of thyristor T3 is:

R3 = Uс/Ig = 31/0,015 = 2066 Ω;

A resistor of 2.1 kΩ is selected.

- The capacitor capacitance is determined considering the time constant of the R3 and C circuit. With τ=0.06s, the required capacitance is: C≈28μF [55].

A DC capacitor rated at 50 V with capacitance 33μF is selected.

- From the secondary winding voltage of the transformer, two identical low-power thyristors type KU201V are selected.

Elektrical parameters of KU201V [2, 56]:

- Maximum forward/reverse voltage: 50 V;

- Maximum gate current: 100 mA;

- Load current: 2 A.

9. We determine from the control current of the low-power thyristors and the nominal voltage of the secondary winding of the low-power transformer the value of the minimum resistance of the control resistors R. The minimum resistance of the gate resistors is determined as:

R1=R2=U2Ig.max / Ig.max=24/0.1=240 Ω

- Based on the maximum secondary voltage and the gate current of the low-power thyristor, a diode type D7A is selected, with Id=30 mA and Urev.max.=50 V.

- For the control transformer, the initial data are:

- Primary voltage: U1=220 V;

- Secondary voltage: U2=24 V;

- Maximum load current: I2=0.3A (according to the control current of the power thyristor).

- The secondary power is:

Sout=U2⋅I2=24⋅0.3=7.2VA

- The magnetic core dimensions are calculated using Eq. (4).

sm4

Assuming: Bmax=1.3T, J=3.7A/mm2, Kwf=0.24, Kst=0.85.

FIGURE 1. Magnetic core

From [1], a core type Ш12×16 (Fig.1), is selected with Scs Swa=6.8 cm4, Sst,ef =1.92 cm2, and Gst=0.140 kg.

Core dimensions (mm): a=12, h=30, c=12, C=48, H=42, B=16.

- The rated primary current is:

[А],

Where the values of η and cosφ are dependent on the transformer power and can be approximately taken as η=0.65; cosφ=0.89.

- The winding conductor cross-sectional areas:

[mm2],      [mm2]

- The conductor diameters:

[mm],

[mm]

Standard wire diameters of 0.45 mm and 0.69 mm (type PEL) are selected.

| FIGURE 2. The schematic diagram STVR | FIGURE 3. The “input–output” characteristic STV |
| --- | --- |

- The number of turns of the transformer windings is determined from Eq. (8).

As a result of the calculation, the following STVR elements were selected:

- Power thyristor: VT3 type 151-500R

- Bridge diodes: D246B

- Series resistor: R3=2.1kΩ

- Capacitor: 50 V, 33 μF

- Low-power thyristors: VT1 and VT2 type KU201V

- Control diode: D7A

- R1=3kΩ

- Resistor R2=5 kΩ.

The schematic diagram of the STVR is shown in Figure 2. The “input-output” characteristic of the fabricated STVR, designed according to the calculation results, is shown in Figure 3 [1-13, 57].

CONCLUSION

Based on the analysis of existing literature on the calculation of elements in contactless switching devices, it has been established that when selecting semiconductor components, resistors, and capacitors, their maximum load operating conditions must be taken into account. The calculation of the input transformer of the thyristor-based solid-state voltage relay (STVR) is most appropriately carried out starting from the determination of the magnetic core dimensions, using specified values of magnetic induction and current density. The selection of thyristors, diodes, and resistors should be made according to rated power, voltage, and calculated current values. The capacitor selection is based on the secondary winding voltage of the input transformer, taking into account the time constant of the R3-C circuit.

Experimental investigations have demonstrated that the developed alternating-current thyristor-based solid-state voltage relay exhibits high values of reset ratio and multiplicity factor, while ensuring reliable operation under significant nominal switching power.

REFERENCES

1. I.I.Belopolsky, E.I.Karetnikova, L.G.Pikalova. Calculation of transformers and low-power chokes. Moscow, Energiya, (1973), p.400.

2. A.V.Bayukov, A.B.Gitsevich, A.A.Zaitsev, and others. Semiconductor devices: Diodes, thyristors, optoelectronic devices. Under the general editorship of N.N.Goryunov, Moscow: Energoatomizdat, (1985), p.744

3. E.X.Abduraimov, A.A.Alimov, A.M.Adxamov, S.A.Dusmukhamedova. Application of Semiconductor Contactless Devices to Improve the Quality and Reliability of Power Supply Systems. AIP Conference Proceedings, 3152(1), 040023, (2024), https://doi.org/10.1063/5.0218898

4. A.A.Alimov, E.X.Abduraimov, F.A.Akbarov, D.A.Nosirova. Analysis of the Basic Circuit of Ferroresonant Transistor Parametric Dc Voltage Stabilizers with Built - in Functional Converter. AIP Conference Proceedings, 3152(1), 050016, (2024), https://doi.org/10.1063/5.0218823

- 5. E.Kh.Abduraimov, and others. Theoretical research and development optoelectronic communication devices, Journal of Physics: Conf.: Ser. 1515, 022055, (2020). doi:10.1088/1742-6596/1515/2/022055

- 6. E.Kh.Abduraimov. Research of the trigger effect in diode-thyristor circuits of contactless relay devices. E3S Web of Conferences 216, 01105, (2020). https://doi.org/10.1051/e3sconf/202021601105

- 7. E.Kh.Abduraimov, D.Kh.Khalmanov. Development of contactless solid state voltage relay. E3S Web of Conferences, 216, 01106, (2020). https://doi.org/10.1051/e3sconf/202021601106

- 8. E.Abduraimov, and others. Control of quality and modes of power supply systems using contactless devices. E3S Web of Conf.: 289, 07026, (2021), https://doi.org/10.1051/e3sconf/202128907026

- 9. E.Kh.Abduraimov, and others. Analysis of dynamic circuits of contactless switching devices. Journal of Physics: Conference Series. 2094, 022072, (2021). IOP Publishing doi:10.1088/1742-6596/2094/2/022072

- 10. E.Kh.Abduraimov. Automatic control of reactive power compensation using a solid state voltage relays. J.Phys.: Conf. Ser. 2373, 072009, (2022). IOP Publishing doi:10.1088/1742-6596/2373/7/072009

- 11. E.Kh.Abduraimov, and D.Kh.Khalmanov. Invention of a contactless voltage relay with an adjustable reset ratio. J.Phys.: Conf. Ser. 2373, 072010, (2022). IOP Publishing doi:10.1088/1742-6596/2373/7/072010

- 12. E.Kh.Abduraimov, and others. Development of contactless device for maintaining the rated voltage of power supply systems. Cite as: AIP Conference Proceedings, 2552, 040012, (2023). https://doi.org/10.1063/5.0116235

13. E.Kh.Abduraimov. Efficient protection and control of electric drives using solid state circuits. E3S Web of Conferences, 384, 01051, (2023). https://doi.org/10.1051/e3sconf/202338401051

14. E.Kh.Abduraimov, and B.Nurmatov. Application of numerical and graphical methods of analysis in nonlinear resistive circuits of electronic devices. E3S Web of Conferences, 384, 01052, (2023). https://doi.org/10.1051/e3sconf/202338401052

15. K.Abidov, E.Abduraimov, M.Gafurova. Possibility of applying methods of analysis and synthesis of linear electrical circuits to some nonlinear circuits. AIP Conf. Proc. 3331, 040034, (2025). https://doi.org/10.1063/5.0305757

16. A.Alimov, K.Abidov, E.Abduraimov, F.Akbarov, H.Muminov. Generalized model of nonlinear inductance and its parameters. AIP Conf. Proc. 3331, 040035, (2025). https://doi.org/10.1063/5.0305883

17. F.Akbarov, R.Kabulov, A.Alimov, E.Abduraimov, D.Nasirova. Dependence of Output Parameters of Photovoltaic Module Based on CIGS Solar Cells on External Temperatures. AIP Conference Parameters, 3331(1), 040046, (2025), https://doi.org/10.1063/5.0305885

18. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, D.Xalmanov, Y.Shoyimov, D.Khimmataliev. Mathematical Models and Calculation of Elements of Developed Schemes of Contactless Devices. AIP Conference Proceedings, 3331(1), 040043, (2025), https://doi.org/10.1063/5.0305748

19. A.Nuraliyev, I.Jalolov, M.Peysenov, A.Adxamov, S.Rismukhamedov, R.Karimov. Improving and Increasing the Efficiency of the Industrial Gas Waste Cleaning Electrical Filter Device. AIP Conference Proceedings, 3331(1), 040040, (2025), https://doi.org/10.1063/5.0305751

20. E.Yuldashev, M.Yuldasheva, A.Togayev, J.Abdullayev, R.Karimov. Energy efficiency research of conveyor transport. AIP Conference Proceedings, 3331(1), 040030, (2025), https://doi.org/10.1063/5.0305742

21. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. Development of Contactless Device Schemes for Automatic Control of the Power of a Capacitor Battery. AIP Conference Proceedings, 3331(1), 040042, (2025), https://doi.org/10.1063/5.0305879

22. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. Review of Literature Sources and Internet Materials on Contactless Devices for Reactive Power Compensation. AIP Conference Proceedings, 3331(1), 040041, (2025), https://doi.org/10.1063/5.0305878

23. M.Sadullaev, M.Bobojanov, R.Karimov, D.Xushvaktov, Y.Shoyimov, H.Achilov. Experimental Studies of Contactless Devices for Controlling the Power of Capacitor Batteries. AIP Conference Proceedings, 3331(1), 040044, (2025), https://doi.org/10.1063/5.0307195

24. E.Usmanov, M.Bobojanov, R.Karimov, D.Xalmanov, N.Tairova, S.Torayev. Contactless Switching Devices Using Nonlinear Circuits. AIP Conference Proceedings, 3331(1), 040031, (2025), https://doi.org/10.1063/5.0305744

25. K.Abidov, A.Alimov, M.Gafurova. Transients in Devices of Control Systems With Excitation Winding. AIP Conference Proceedings, 3331(1), 040033, (2025), https://doi.org/10.1063/5.0305756

26. O.Ishnazarov, N.Khamudkhanova, K.Kholbutayeva, K.Abidov. Energy Efficiency Optimization in Irrigation Pump Installations. AIP Conference Proceedings, 3331(1), 040036, (2025), https://doi.org/10.1063/5.0305844

27. K.Abidov, A.Alimov, N.Khamudkhanova, M.Gafurova. Determination of the Permissible Number of Pumping Units Supplied From the Transformer of the Amu-Zang-I Substation, Selection of the Power of Static Capacitors. AIP Conference Proceedings, 3331(1), 040029, (2025), https://doi.org/10.1063/5.0305754

28. Y.Adilov, A.Nuraliyev, M.Abdullayev, S.Matkarimov. Dynamic Performance Model of a Hybrid Power System. AIP Conference Proceedings, 3331(1), 040038, (2025). https://doi.org/10.1063/5.0305909

29. Y.Adilov, M.Khabibullaev. Application of fiber-optic measuring current transformer in control and relay protection systems of belt conveyor drives. IOP Conference Series Earth and Environmental Science, 614(1), 012022, (2020), doi:10.1088/1755-1315/614/1/012022

30. R.Yusupaliyev, N.Musashayxova, A.Kuchkarov. Methods of Purification of Polluted Water from Ammonia Compounds at Nitrogen Fertilizer Plants. E3S Web of Conferences, 563, 03085, (2024). https://doi.org/10.1051/e3sconf/202456303085

31. S.M.Turabdzhanov, J.M.Tangirov, P.M.Matyakubova, N.S.Amirkhulov, S.S.Khabibullaev. Methods of providing metrological supply when pumping water into wells in oil fields. AIP Conference Proceedings, 3045(1), 030073, (2024), https://doi.org/10.1063/5.0197355

32. R.Yusupaliev, B.Yunusov, M.Azimova. The composition of natural waters of some source rivers of the republic of Uzbekistan, used in the thermal power engineering and the results of the experimental researches at preliminary and ion exchange treatment of water. E3S Web of Conferences, 139, 01083, (2019), https://doi.org/10.1051/e3sconf/201913901083

33. R.Yusupaliev, N.Kurbanova, M.Azimova, N.Musashaikhova, A.Kuchkarov. Establishing a Water-chemical Regime and Increasing the Efficiency of Combustion of a Mixture of Fuel Oil and Gas in a DE 25-14 GM Boiler: A Case Study of the Kokand Distillery. AIP Conference Proceedings, 2552, 030026, (2022). https://doi.org/10.1063/5.0130471

34. M.Azimova, N.Kurbanova, D.Rakhmatov. Large-scale environmental benefits of biogas technology. AIP Conference Proceedings, 3152(1), 060007, (2024), https://doi.org/10.1063/5.0218937

35. M.Jalilov, M.Azimova, A.Jalilova. On a new technology of preparation of hot drinking water. Energetika Proceedings of Cis Higher Education Institutions and Power Engineering Associations, 60(5), (2017), pp.484-492. https://doi.org/10.21122/1029-7448-2017-60-5-484-492

36. S.Amirov, A.Sulliev, U.Mukhtorov. Resonance sensors of motion parameters. AIP Conference Proceedings, 3256(1), 050028, (2025). https://doi.org/10.1063/5.0267548

37. K.Turdibekov, A.Sulliev, O.Iskandarova, J.Boboqulov. Experimental and statistical methods for studying the modes of electric power systems under conditions of uncertainty. E3S Web of Conferences, 452, 04002, (2023), https://doi.org/10.1051/e3sconf/202345204002

38. S.Amirov, A.Sulliev, S.Sharapov. Study on differential transformer displacement sensors. E3S Web of Conferences, 434, 02011, (2023), https://doi.org/10.1051/e3sconf/202343402011

39. S.Kasimov, A.Sulliev, A.Eshkabilov. Optimising Pulse Combustion Systems for Enhanced Efficiency and Sustainability in Thermal Power Engineering. E3S Web of Conferences, 449, 06006, (2023), https://doi.org/10.1051/e3sconf/202344906006

40. S.Amirov, A.Sulliev, K.Turdibekov. Investigation of biparametric resonance sensors with distributed parameters. E3S Web of Conferences, 377, 01002, (2023), https://doi.org/10.1051/e3sconf/202337701002

41. M.Yakubov, A.Sulliev, A.Sanbetova. Modern methods of evaluation of metrological indicators of channels for measurement and processing of diagnostic values of traction power supply. IOP Conference Series Earth and Environmental Science, 1142(1), 012010, (2023), doi:10.1088/1755-1315/1142/1/012010

42. K.Turdibekov, A.Sulliev, I.Qurbanov, S.Samatov, A.Sanbetova. Voltage Symmetration in High Speed Transport Power Supply Systems. AIP Conference Proceedings, 2432, 030084, (2022), https://doi.org/10.1063/5.0089958

43. K.Turdibekov, M.Yakubov, A.Sulliev, A.Sanbetova. Mathematical Models of Asymmetric Modes in High-Speed Traffic. Lecture Notes in Networks and Systems, 247, (2022), pp.1051-1058. DOI:10.1007/978-3-030-80946-1_95

44. S.K.Shah, L.Safarov, A.Sanbetova, and etc. Investigation on composite phase change materials for energy-saving buildings. E3S Web of Conferences, 563, 01003, (2024), https://doi.org/10.1051/e3sconf/202456301003

45. A.Sanbetova, A.Mukhammadiev, A.Rakhmatov, Z.Beknazarova. Study on cultivation of environmentally friendly seed potatoes based on electrical technology. E3S Web of Conferences, 377, 03001, (2023), https://doi.org/10.1051/e3sconf/202337703001

46. G.Boboyev, N.Inatova. The Importance of Implementing Energy Management Systems for Manufacturing Enterprises in the Republic of Uzbekistan. AIP Conference Proceedings, 3331(1), 040047, (2025). https://doi.org/10.1063/5.0305865

47. G.Boboyev, N.Nurmukhamedov, O.Zaripov. Improvement of Means of Measuring the Main Parameters of Electricity. AIP Conference Proceedings, 3331(1), 040039, (2025). https://doi.org/10.1063/5.0305861

48. A.T.Rakhmanov, G.G.Boboev. Developing the Technology for Manufacturing Ohmic Contacts and Sealing Semiconductor Temperature Converters. Journal of Engineering Physics and Thermophysics, 98(3), (2025), pp.841-845. https://doi.org/10.1007/s10891-025-03163-6

49. N.I.Avezova, P.R.Ismatullayev, P.M.Matyakubova, G.G Boboyev. Multifunctional Heat Converter Moisture Content of Liquid Materials. International Conference on Information Science and Communications Technologies Applications Trends and Opportunities Icisct 2019, 9012041, (2019). DOI: 10.1109/ICISCT47635.2019.9012041

50.  M.Mirsadov, B.Fayzullayev, I.Abdullabekov, A.Kupriyanova, D.Kurbanbayeva, U.Boqijonov. The mutual influence of electromagnetic and mechanical processes in dynamic modes of inertial vibrating electric drives. IOP Conference Series Materials Science and Engineering, 862(6), 062081, (2020). doi:10.1088/1757-899X/862/6/062081

51. I.Abdullabekov, M.Mirsaidov, F.Tuychiev, R.Dusmatov. Frequency converter – asynchronous motor – pump pressure piping system mechanical specifications. AIP Conference Proceedings, 3152, 040007 (2024). https://doi.org/10.1063/5.0218880

52. I.Abdullabekov, M.Mirsaidov, Sh.Umarov, M.Tulyaganov, S.Oripov. Optimizing energy efficiency in water pumping stations: A case study of the Chilonzor water distribution facility. AIP Conference Proceedings, 3331, 030107, (2025). https://doi.org/10.1063/5.0305780

53. M.Bobojanov, F.Tuychiev, N.Rashidov, A.Haqberdiyev, I.Abdullabekov. Dynamic simulation of a three-phase induction motor using Matlab Simulink. AIP Conference Proceedings, 3331, 040012, (2025). https://doi.org/10.1063/5.0305750

54. M.Tulyaganov, Sh.Umarov, I.Abdullabekov, Sh.Adilova. Optimization of modes of an asynchronous electric drive taken into account thermal transient processes. AIP Conference Proceedings, 3331, 030084, (2025). https://doi.org/10.1063/5.0305786

55. Sh.Umarov, Kh.Sapaev, I.Abdullabekov. The Implicit Formulas of Numerical Integration Digital Models of Nonlinear Transformers. AIP Conference Proceedings, 3331, 030105, (2025), https://doi.org/10.1063/5.0305793

56. Web of Conferences, 216, 01093, (2020). https://doi.org/10.1051/e3sconf/202021601093

56. J.Safarov, Sh.Sultanova, G.Dadayev, Sh.Zulponov. Influence of the structure of coolant flows on the temperature profile by phases in a water heating dryer. IOP Conf. Series: Materials Science and Engineering, 1029(1), 012019, (2021). doi:10.1088/1757-899X/1029/1/012019

57. Sh.Sultanova, A.Artikov, Z.Masharipova, A.Tarawade, J.Safarov. Results of experiments conducted in a helio water heating convective drying plant. IOP Conf. Series: Earth and Environmental Science, 868(1), 012045, (2021). doi:10.1088/1755-1315/868/1/012045