Calculation Methodology for Voltage-Boosting Transformer Voltage Stabilizer

Erkin Abduraimov 1,a), Anvar Alimov 1,2, Golibjon Arzikulov 1,

Kholjan Kholbutayeva 1, Umida Akberadjieva 1

1 Tashkent state technical university named after Islam Karimov, Tashkent, Uzbekistan

2 Almalyk State Technical Institute, Almalyk, Uzbekistan

a) Corresponding author: abduraimoverkin69@gmail.com

Abstract. This paper presents a developed methodology for calculating voltage-boosting transformers for application in the development of contactless voltage stabilizers, where the control of voltage-boosting windings is implemented using contactless voltage relays. The calculation methodology is based on existing literature on transformer design, while addressing the selection of optimal parameters for voltage-boosting transformers in voltage stabilizers, considering the share of installed transformer power relative to the output load power. The paper provides thermal calculation methodology and determination of voltage-boosting transformer parameters.

INTRODUCTION

The main element of the proposed voltage stabilizer circuit is the voltage-boosting transformer. Below is a calculation methodology based on existing literature on transformer design. It is considered that the installed power of the voltage-boosting transformer is within 25÷30% of the output power of the voltage stabilizer [1-3, 21-27].

For calculating the voltage-boosting transformer, the following initial data must be specified [4-7, 33]:

- Supply voltage – U1;

- Supply frequency – fsupply;

- Secondary winding voltage – U2;

- Secondary winding current – I2;

- Load characteristic;

- Ambient temperature – tamb, 0C.

CALCULATION METHOD

For calculating voltage-boosting transformers with armoured and core-type magnetic circuits for a specified temperature rise, the following calculation procedure is recommended [8-13, 28-32, 34].

Determine the required secondary winding power:

S2=U2·I2, VA							(1)

Tables 1 and 2 present the types of magnetic circuit construction that have found the greatest application in manufacturing low-power transformers. From these tables, select the steel grade and thickness of the magnetic circuit plate or tape according to the specified supply frequency. Based on the found value S₂ for the given magnetic circuit construction, find approximate values of Bmax, δ, kwf, kst [1-3, 14-20, 35-38].

- Bmax - [T] magnetic induction (Table 1);

- δ - [A/mm²] current density (Table 2);

- kwf - window fill factor (Table 3);

- kst - magnetic circuit fill factor (Table 4);

Using the following formula, find the product of the steel cross-sectional area of the magnetic circuit (Sst) and its window area (Swa):

[sм4]; 				(2)

TABLE 1. Types of magnetic circuit designs for selecting steel grades and plate thicknesses for a given frequency

| Magnetic Circuit Construction | Core Material and Thickness, mm | supply Frequency, Hz | Magnetic Induction Bmax, Tl, for S2, VA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 5-15 | 15-50 | 50-150 | 150-300 | 300-1000 | 1000-2500 |
| Armored (laminated) | E42, Δ=0.35 | 50 | 1,1–1,3 | 1,3 | 1,3 –1,35 | 1,35 | 1,35–1,2 | – |
| Armored (tape) | E310, Δ=0.35 | 50 | 1,55 | 1,65 | 1,65 | 1,65 | 1,65 | – |
| Core-type (tape) | E310, Δ=0.35 | 50 | 1,5–1,6 | 1,6 | 1,7 | 1,7 | 1,7 | 1,7 |

TABLE 2. Recommended current density values for the magnetic circuit configuration

| Magnetic Circuit Construction | Core Material and Thickness, mm | supply Frequency, Hz | Current Density δ, A/mm², for S2, VA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 5-15 | 15-50 | 50-150 | 150-300 | 300-1000 | 1000-2500 |
| Armored (laminated) | E42, Δ=0.35 | 50 | 3,9–3,0 | 3,0–2,4 | 2,4 –2,0 | 2,0–1,7 | 1,7–1,4 | – |
| Armored (tape) | E310, Δ=0.35 | 50 | 3,8–3,5 | 3,5–2,7 | 2,7–2,4 | 2,4–2,3 | 2,3–1,8 | – |
| Core-type (tape) | E310, Δ=0.35 | 50 | 7–5,2 | 5,2–3,8 | 3,8–3,0 | 3,0–2,4 | 2,4–1,7 | 1,7–1,4 |

TABLE 3. Window Fill Factor by Magnetic Core Construction and Operating Voltage

| Magnetic Circuit Construction | Operating voltage, V | Window Fill Factor kwin for S2, VA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 5–15 | 15–50 | 50–150 | 150–300 | 300–1000 | 1000–2500 |
| Armored (laminated) | Up to 10 From 100 to 1000 | 0,22–0,29 0,19–0,25 | 0,29–0,30 0,25-0,26 | 0,3-0,32 0,26-0,27 | 0,32-0,34 0,27-0,30 | 0,34-0,38 0,30-0,33 | – – |
| Armored (tape) | Up to 100 From 100 to 1000 | 0,15-0,27 0,13-0,23 | 0,27-0,29 0,23-0,26 | 0.29-0,32 0,26-0,27 | 0,32-0,34 0,27-0,30 | 0,34-0,38 0,30-0,33 | – – |
| Core-type (tape) | Up to 100 From 100 to 1000 | 0,14-0,25 0,12-0,21 | 0,25-0,28 0,21-0,24 | 0,28-0,29 0,24-0,25 | 0,29-0,30 0,25-0,30 | 0,30-0,35 0,30 | 0,35 0,30 |

TABLE 4. Magnetic core filling factor according to magnetic core design

| Magnetic Circuit Construction | Kst magnetic core filling coefficient for steel thickness, mm |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 0,08 | 0,1 | 0,15 | 0,2 | 0,35 |
| Core-type, armored (laminated) | – | 0,7 (0,75) | – | 0,85 (0,89) | 0,9 (0,94) |
| Core-type, armored (tape) | 0,87 | – | 0,9 | 0,91 | 0,93 |

From table 5, extract the necessary data: a, h, c, C, H, B [1-3, 21-27, 43].

Steel losses for induction Bmax:

Pst=ρst Gst  [Wt],						(3)

where ρst - specific losses (per 1 kg of steel), determined from the curve in Fig.1.

Find the active component of the no-load current using the formula for maximum supply voltage, considering Pst=Iоа U1 [Wt]:

[А],						(4)

TABLE 5. Reference values and dimensions of the magnetic circuit

| Magnetic Circuit | Dimensions, mm |  |  |  |  |  | Reference Values |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | Magnetic circuit cross-section, sm2 | The average length of the magnetic circuit, sm | Cross-sectional area of steel x window area sm4 | Magnetic core volume, sm2 | Weight magnetic circuit kg | Approximate transformer capacity |  |
|  |  |  |  |  |  |  |  |  |  |  |  | =50 | =400 |
|  | а | h | c | C | H | B | Sst | Lst | Sst Swa | Vst | Gst | P2 |  |
| EI core 25×32 | 25 | 62,5 | 25 | 100 | 87,5 | 32 | 8 | 21,3 | 125 | 170 | 1,17 | 135 | 730 |
| EI core 25×40 |  |  |  |  |  | 40 | 10 |  | 156 | 213 | 1,47 | 170 | 810 |
| EI core 25×50 |  |  |  |  |  | 50 | 12 |  | 195 | 266 | 1,84 | 210 | 990 |

FIGURE 1. Specific magnetizing power Specific losses in cores made of transformer steels with a thickness of 0.35 mm at a frequency of 50 Hz. 1 - E42 steel armor cores: 2 - E310 steel core cores: 3 - E310 steel armor cores types of steel armor cores: 1 - E42, 0.35 mm thick, f-50 Hz; 2 - E44, 0.2 mm thick, 400 Hz; 3 - E340, 0.15 mm thick, f-400 Hz.

Find the total magnetizing power using the following formula:

Qst=qst Gst  [VА],						(5)

where qst - total specific magnetizing power [VA/kg] from curves in Fig.2 [1, 28-34, 39-42].

FIGURE 2. Specific magnetizing power for steel armor cores: 1 - E42, 0.35 mm thick, f-50 Hz; 2 - E44, 0.2 mm thick, 400 Hz; 3 - E340, 0.15 mm thick, f-400 Hz

Determine the reactive component of no-load current, knowing that:

[VAr]					(6)

Find the no-load current value using the formula:

, [А]					(7)

Nominal current of the primary winding:

(8)

where Р2 is the power of the secondary winding;

TABLE 6. Efficiency and power factor of the total power of the secondary windings.

| Supply Frequency, Hz | Values | Total Secondary Winding Power P2, Wt |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 2-15 | 15-50 | 50-150 | 150-300 | 300-1000 | 1000-2500 |
| 50 | соs | 0,5-0,6 0,85-0,90 | 0,6-0,8 0,9; 0,93 | 0,8-0,9 0,93; 0,95 | 0,9-0,93 0,95-0,93 | 0,93-0,95 0,93-0,94 | - - |

Find the number of turns in windings:

(9)

(10)

Here E1 = U1(1-ΔU1); E2 = U2(1+ΔU2).

where ΔU1 and ΔU2 - voltage drops in windings.

TABLE 7. The magnitude of the voltage drop in the total power of the secondary windings

| Supply Frequency, Hz | Magnetic Circuit Construction | Values | Total Secondary Winding Power P2, Wt |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 5-15 | 15-50 | 50-150 | 150-300 | 300-1000 | 1000-2500 |
| 50 | Shell type | ΔU1 % ΔU2 % | 20-13 25-18 | 13-6 18-20 | 6–-4,5 10-8 | 4.5-3 8-6 | 3-1 6-2 | – – |
|  | Core type | ΔU1 % ΔU2 % | 18-12 33-17 | 12-5,5 17-9 | 5,5-4 9-6 | 4-3 6-4 | 3-1 4-2 | 1-0,8 2-1,0 |

Using Table 2, find the recommended current density values in windings δ1, δ2 for the selected magnetic circuit configuration [1-3, 21-27, 43-47].

Determine cross-sections and diameters of winding conductors using the following relationships:

, mm2						(11)

mm2				(12)

From Table 8, select standard cross-sections and conductor diameters and extract necessary reference data [1].

After selecting standard cross-sections and conductor diameters, find actual current densities in conductors:

А/mm2;          А/mm2

The allowable axial length of each winding on the sleeve is determined using the following formula:

hD=h1−2hins ,						(13)

where h1 = h - 1 mm - length of the sleeve; h - window height; hins - end insulation length equal to 1.5÷3 mm.

From Fig.3, select axial laying coefficients kl1 depending on selected winding conductor diameters [48-55].

Determine the number of turns per layer and number of layers for each winding:

,						(14)

(15)

where kl1 - axial conductor laying coefficient determined from Fig.5 data; W - total number of winding turns.

TABLE 8. Nominal values and parameters of the copper conductor.

| nominal copper wire diameter, mm | Calculated cross- section, mm² | Mass of 1m Wire,g | DC Resistance, Ω/m | Maximum Outer Diameter for Different Insulations, mm, |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Pel | Pev-1 | Pev-2 | PEVTL1 | PEVTL2 | PETV | PELSHO | PELLO | PEPLO , PETLO | PEVLO | PNET- imid |
| 0,90 | 0,6362 | 5,66 | 0,0270 | 0,99 | 0,96 | 0,99 | 0,96 | 0,99 | 0,99 | 1,05 | 1,05 | 1,09 | 1,07 | 0,96 |
| 0,93 | 0,6793 | 6,04 | 0,0253 | 0,99 | 0,99 | 1,02 | 0,99 | 1,02 | 1,02 | 1,08 | 1,08 | 1,12 | 1,10 | 0,99 |
| 0,96 | 0,7238 | 6,44 | 0,0238 | 1,02 | 1,02 | 1,05 | 1,02 | 1,05 | 1,05 | 1,11 | 1,11 | 1,15 | 1,13 | 1,02 |
| 1,00 | 0,7854 | 6,98 | 0,0219 | 1,07 | 1,08 | 1,11 | 1,08 | 1,11 | 1,11 | 1,16 | 1,16 | 1,20 | 1,19 | 1,06 |
| 1,56 | 1,9113 | 17,0 | 0,0091 | 1,64 | 1,64 | 1,67 | 1,64 | 1,67 | 1,67 | 1,74 | - | - | - | - |
| 2,44 | 4,676 | 41,6 | 0,0037 | 2,54 | 2,54 | 2,57 | - | - | 2,57 | - | - | - | - | - |
| 2,63 | 5,433 | 48,3 | 0.0032 | - | - | 2,76 | - | - | - | - | - | - | - | - |
| 2,83 | 6,290 | 55,9 | 0.0027 | - | - | - | - | - | - | - | - | - | - | - |
| 3,05 | 7,306 | 65 | 0,0024 | - | - | - | - | - | - | - | - | - | - | - |

FIGURE 3. Dependence of the laying coefficient in the axial direction on the diameter of the wire

From Fig.4, determine kb=b/a (applicable only when winding on the sleeve).

Select insulation distances hins1, hins.bw, hins.ax, and hins.out using recommendations given in [1, 56-58].

FIGURE 4. Dependence of the bulging coefficient in the radial direction on the diameter of the wire and the sleeve design

From Figs.5-6, determine radial laying coefficients (kl2) and interlayer and interwinding insulation expansion coefficients (kil and kiw) depending on winding conductor diameters:

Find radial dimensions of each winding using the formula:

αi = kl2 · N · dins + kil (N-1)hins.mc , mm				(16)

Assume outer insulation winding compaction coefficient values kr.b = 1.7÷2.0.

Determine coil radial dimension using the following formula:

α = Δgap + (hins.ax + α1 + kiw·h'ins.bw + α2 + kiw·h''ins.bw + kic·hins.out) krb		(17)

where:

- Δgap = 0.5 mm - gap between bobbin and core

- hins.ax - bobbin thickness including additional insulation over frame

- α1, α2 - winding radial dimensions, mm

- h'ins.bw, h''ins.bw - interwinding insulation thickness, mm

- hins.out - outer insulation thickness

- kic - interwinding insulation compaction coefficient

- krb - radial bulging coefficient

FIGURE 5. Dependence of the coefficient of laying in the radial direction on the diameter of the wire.

FIGURE 6. Dependence of the coefficient of leakage of the inter-winding insulation on the wire diameter

Determine the gap between coil and core (for armored transformers) or between two coils (for core-type transformers).

Determine total copper losses in windings using formulas and Table 9:

Pcop = Pcop1 + Pcop2					(18)

Pcop ≈ m·δ²·Gcop						(19)

TABLE 9. The temperature and length of the conductor for calculating the copper loss of the windings.

| tconductor, °C | 90 | 105 | 120 | 130 | 155 | 180 | 200 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| m | 2,52 | 2,65 | 2,76 | 2,84 | 3,02 | 3,23 | 3,38 |

a) Find average turn length for each winding using the following formulas:

, m.				(20)

where     , and ;     ;

, m.			(21)

where      mm.

b) Find copper mass for each winding:

, kg,				(22)

where lav.T - average turn length, m; W - total number of winding turns; gcopper - mass of 1m wire, g

THERMAL CALCULATION

Determine thermal resistances from Table 10 data [1, 58-62].

TABLE 10. Thermal resistances according to standard sizes of magnetic circuit’s type

| Magnetic circuit type | Rframe | Rcore | Rcore° | Rsteel° |
| --- | --- | --- | --- | --- |
|  | °С/Wt |  |  |  |
| EI core 25×40 EI core 32Х40 EI core 32Х50 EI core 32Х64 | 1,7 1,1 0,9 0,8 | 1,0 0,8 0,7 0,7 | 4,0 2,5 2,5 2,5 | 3,1 2,1 1,8 1,5 |

Determine coil-to-core heat flow using the formula:

, Wt.				(23)

Determine coil thermal resistance from maximum heated area to bobbin using the following formula:

,°С/Wt,		(24)

According to thermal calculation methodology [1], determine heat flow from core to coil Pc”  using the formula:

,   Wt.					(25)

If  value is positive, determine maximum coil temperature rise using the formula:

,°С.				(26)

Determine average temperature difference in coil using the formula:

°С.					(27)

Determine average volumetric coil temperature rise using the formula:

°С,						(28)

;

where Θ₁ - temperature difference in primary winding, °C

Determine maximum and average conductor temperatures:

tcon.max=50+ °С;        tcon.av=50+  °С;

If the maximum allowable temperature does not exceed the permissible temperature based on the calculation, the wire grades adopted in the calculation can be used in this transformer.

Determine active winding resistances using the formula:

, Ω						(29)

at tconductor = 105°C, ρcopper = 2.35×10⁻² Ω·mm²/m

DETERMINATION OF VOLTAGE-BOOSTING TRANSFORMER PARAMETERS

Determine total active resistances of transformer winding pairs referred to primary winding using the relationship [1-3, 21-27, 57-65]:

, Ω					(30)

Determine leakage reactance’s of transformer winding pairs using the formula:

, Ω				(31)

where g11 and g22 - average geometric distances of winding cross-sections from their mirror images; g12 - average geometric distances between winding cross-sections; ks - coefficient accounting for steel core influence on leakage inductance; lavg.coil - average coil turn length

g11 ≈ 0.2235(hallowable1 + α₁),					(32)

g22 ≈ 0.2235(hallowable2 + α₂),					(33)

g12 ≈ 0.78d + 0.2235hallowable,					(34)

where

d = h'ins.mo + (α1 + α₂)/2						(35)

Determine coefficient ks accounting for ferromagnetic core influence:

,		(36)

, m				(37)

Determine absolute and relative values of active and reactive voltage drop components in windings:

, %						(38)

, %						(39)

Transformer efficiency is determined using the formula:

%					(40)

Total voltage drop in transformer can be approximately found through winding voltage drops:

, %	(41)

Based on voltage-boosting transformer calculation results, prepare winding specification and testing data table.

CONCLUSION

Thus, based on analysis of existing literature materials, a calculation methodology for voltage-boosting transformer voltage stabilizers has been developed and proposed. Selection of optimal VBT voltage stabilizer parameters is performed considering the share of installed transformer power relative to output load power. Based on the developed methodology, a computer program for calculating voltage-boosting voltage stabilizers has been compiled. Test results of the manufactured voltage-boosting voltage stabilizer prototype showed that the proposed methodology is sufficiently accurate and acceptable for practical use.

REFERENCES

1. E.X.Abduraimov, A.A.Alimov, A.M.Adxamov, S.A.Dusmukhamedova. Application of Semiconductor Contactless Devices to Improve the Quality and Reliability of Power Supply Systems. AIP Conference Proceedings, 3152(1), 040023, (2024), https://doi.org/10.1063/5.0218898

2. I.I.Belopolsky, E.I.Karetnikova, L.G.Pikalova. Calculation of transformers and low-power chokes. Moscow, Energiya, (1973), p.400.

3. E.Kh.Abduraimov, and others. Development of contactless device for maintaining the rated voltage of power supply systems. Cite as: AIP Conference Proceedings 2552, 040012, (2023). https://doi.org/10.1063/5.0116235

4. S.B.Vasyutinsky. Questions of theory and calculation of transformers. Moscow, Energia, (1970).

5. A.A.Alimov, E.X.Abduraimov, F.A.Akbarov, D.A.Nosirova. Analysis of the Basic Circuit of Ferroresonant Transistor Parametric Dc Voltage Stabilizers with Built - in Functional Converter. AIP Conference Proceedings, 3152(1), 050016, (2024), https://doi.org/10.1063/5.0218823

6. E.Kh.Abduraimov, and others. Theoretical research and development optoelectronic communication devices, Journal of Physics: Conf.: Ser. 1515, 022055, (2020). doi:10.1088/1742-6596/1515/2/022055

7. E.Kh.Abduraimov. Research of the trigger effect in diode-thyristor circuits of contactless relay devices. E3S Web of Conferences, 216, 01105 (2020). https://doi.org/10.1051/e3sconf/202021601105

8. E.Kh.Abduraimov, D.Kh.Khalmanov. Development of contactless solid state voltage relay. E3S Web of Conferences 216, 01106, (2020), https://doi.org/10.1051/e3sconf/202021601106

9. E. Abduraimov, and others. Control of quality and modes of power supply systems using contactless devices. E3S Web of Conf.: 289, 07026, (2021), https://doi.org/10.1051/e3sconf/202128907026

10. E.Kh.Abduraimov, and others. Analysis of dynamic circuits of contactless switching devices. Journal of Physics: Conference Series. 2094, 022072, (2021). IOP Publishing doi:10.1088/1742-6596/2094/2/022072

11. E.Kh.Abduraimov. Automatic control of reactive power compensation using a solid state voltage relays. J.Phys.: Conf. Ser. 2373, 072009, (2022). IOP Publishing doi:10.1088/1742-6596/2373/7/072009

12. E.Kh.Abduraimov, and D.Kh.Khalmanov. Invention of a contactless voltage relay with an adjustable reset ratio. J.Phys.: Conf. Ser. 2373, 072010, (2022). IOP Publishing doi:10.1088/1742-6596/2373/7/072010

13. E.Kh.Abduraimov. Efficient protection and control of electric drives using solid state circuits. E3S Web of Conferences 384, 01051, (2023). https://doi.org/10.1051/e3sconf/202338401051

14. K.Abidov, E.Abduraimov, M.Gafurova. Possibility of applying methods of analysis and synthesis of linear electrical circuits to some nonlinear circuits. AIP Conf. Proc. 3331, 040034, (2025). https://doi.org/10.1063/5.0305757

15. A.Alimov, K.Abidov, E.Abduraimov, F.Akbarov, H.Muminov. Generalized model of nonlinear inductance and its parameters. AIP Conf. Proc. 3331, 040035, (2025). https://doi.org/10.1063/5.0305883

16. F.Akbarov, R.Kabulov, A.Alimov, E.Abduraimov, D.Nasirova. Dependence of Output Parameters of Photovoltaic Module Based on CIGS Solar Cells on External Temperatures. AIP Conference Parameters, 3331(1), 040046, (2025), https://doi.org/10.1063/5.0305885

17. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, D.Xalmanov, Y.Shoyimov, D.Khimmataliev. Mathematical Models and Calculation of Elements of Developed Schemes of Contactless Devices. AIP Conference Proceedings, 3331(1), 040043, (2025), https://doi.org/10.1063/5.0305748

18. E.Yuldashev, M.Yuldasheva, A.Togayev, J.Abdullayev, R.Karimov. Energy efficiency research of conveyor transport. AIP Conference Proceedings, 3331(1), 040030, (2025), https://doi.org/10.1063/5.0305742

19. A.Nuraliyev, I.Jalolov, M.Peysenov, A.Adxamov, S.Rismukhamedov, R.Karimov. Improving and Increasing the Efficiency of the Industrial Gas Waste Cleaning Electrical Filter Device. AIP Conference Proceedings, 3331(1), 040040, (2025), https://doi.org/10.1063/5.0305751

20. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. Development of Contactless Device Schemes for Automatic Control of the Power of a Capacitor Battery. AIP Conference Proceedings, 3331(1), 040042, (2025), https://doi.org/10.1063/5.0305879

21. M.Sadullaev, E.Usmanov, R.Karimov, D.Xushvaktov, N.Tairova, A.Yusubaliev. Review of Literature Sources and Internet Materials on Contactless Devices for Reactive Power Compensation. AIP Conference Proceedings, 3331(1), 040041, (2025), https://doi.org/10.1063/5.0305878

22. K.Abidov, A.Alimov, M.Gafurova. Transients in Devices of Control Systems With Excitation Winding. AIP Conference Proceedings, 3331(1), 040033, (2025), https://doi.org/10.1063/5.0305756

23. O.Ishnazarov, N.Khamudkhanova, K.Kholbutayeva, K.Abidov. Energy Efficiency Optimization in Irrigation Pump Installations. AIP Conference Proceedings, 3331(1), 040036, (2025), https://doi.org/10.1063/5.0305844

24. M.Sadullaev, M.Bobojanov, R.Karimov, D.Xushvaktov, Y.Shoyimov, H.Achilov. Experimental Studies of Contactless Devices for Controlling the Power of Capacitor Batteries. AIP Conference Proceedings, 3331(1), 040044, (2025), https://doi.org/10.1063/5.0307195

25. Y.Adilov, A.Nuraliyev, M.Abdullayev, S.Matkarimov. Dynamic Performance Model of a Hybrid Power System. AIP Conference Proceedings, 3331(1), 040038, (2025). https://doi.org/10.1063/5.0305909

26. E.Usmanov, M.Bobojanov, R.Karimov, D.Xalmanov, N.Tairova, S.Torayev. Contactless Switching Devices Using Nonlinear Circuits. AIP Conference Proceedings, 3331(1), 040031, (2025), https://doi.org/10.1063/5.0305744

27. K.Abidov, A.Alimov, N.Khamudkhanova, M.Gafurova. Determination of the Permissible Number of Pumping Units Supplied From the Transformer of the Amu-Zang-I Substation, Selection of the Power of Static Capacitors. AIP Conference Proceedings, 3331(1), 040029, (2025), https://doi.org/10.1063/5.0305754

28. Y.Adilov, M.Khabibullaev. Application of fiber-optic measuring current transformer in control and relay protection systems of belt conveyor drives. IOP Conference Series Earth and Environmental Science, 614(1), 012022, (2020), doi:10.1088/1755-1315/614/1/012022

29. R.Yusupaliyev, N.Musashayxova, A.Kuchkarov. Methods of Purification of Polluted Water from Ammonia Compounds at Nitrogen Fertilizer Plants. E3S Web of Conferences, 563, 03085, (2024). https://doi.org/10.1051/e3sconf/202456303085

30. R.Yusupaliev, N.Kurbanova, M.Azimova, N.Musashaikhova, A.Kuchkarov. Establishing a Water-chemical Regime and Increasing the Efficiency of Combustion of a Mixture of Fuel Oil and Gas in a DE 25-14 GM Boiler: A Case Study of the Kokand Distillery. AIP Conference Proceedings, 2552, 030026, (2022), https://doi.org/10.1063/5.0130471

31. R.Yusupaliev, B.Yunusov, M.Azimova. The composition of natural waters of some source rivers of the republic of Uzbekistan, used in the thermal power engineering and the results of the experimental researches at preliminary and ion exchange treatment of water. E3S Web of Conferences, 139, 01083, (2019), https://doi.org/10.1051/e3sconf/201913901083

32. Sh.Kuchkanov, M.Adilov, B.Abduraxmanov, A.Kamardin, S.Maksimov, S.Nimatov, and Kh.Ashurov. Thermovoltaic effect in Si/Si epitaxial film structures treated by neon ions. AIP Conference Proceedings, 3331, 040045, (2025). https://doi.org/10.1063/5.0305887

33. M.Azimova, N.Kurbanova, D.Rakhmatov. Large-scale environmental benefits of biogas technology. AIP Conference Proceedings, 3152(1), 060007, (2024), https://doi.org/10.1063/5.0218937

34. M.Jalilov, M.Azimova, A.Jalilova. On a new technology of preparation of hot drinking water. Energetika Proceedings of Cis Higher Education Institutions and Power Engineering Associations, 60(5), (2017), pp.484-492. https://doi.org/10.21122/1029-7448-2017-60-5-484-492

35. S.Amirov, A.Sulliev, U.Mukhtorov. Resonance sensors of motion parameters. AIP Conference Proceedings, 3256(1), 050028, (2025). https://doi.org/10.1063/5.0267548

36. K.Turdibekov, A.Sulliev, O.Iskandarova, J.Boboqulov. Experimental and statistical methods for studying the modes of electric power systems under conditions of uncertainty. E3S Web of Conferences, 452, 04002, (2023), https://doi.org/10.1051/e3sconf/202345204002

37. S.Kasimov, A.Sulliev, A.Eshkabilov. Optimising Pulse Combustion Systems for Enhanced Efficiency and Sustainability in Thermal Power Engineering. E3S Web of Conferences, 449, 06006, (2023), https://doi.org/10.1051/e3sconf/202344906006

38. S.Amirov, A.Sulliev, S.Sharapov. Study on differential transformer displacement sensors. E3S Web of Conferences, 434, 02011, (2023), https://doi.org/10.1051/e3sconf/202343402011

39. S.Amirov, A.Sulliev, K.Turdibekov. Investigation of biparametric resonance sensors with distributed parameters. E3S Web of Conferences, 377, 01002, (2023), https://doi.org/10.1051/e3sconf/202337701002

40. M.Yakubov, A.Sulliev, A.Sanbetova. Modern methods of evaluation of metrological indicators of channels for measurement and processing of diagnostic values of traction power supply. IOP Conference Series Earth and Environmental Science, 1142(1), 012010, (2023), doi:10.1088/1755-1315/1142/1/012010

41. K.Turdibekov, A.Sulliev, , and etc. Voltage Symmetration in High Speed Transport Power Supply Systems. AIP Conference Proceedings, 2432, 030084, (2022), https://doi.org/10.1063/5.0089958

42. S.K.Shah, L.Safarov, A.Sanbetova, and etc. Investigation on composite phase change materials for energy-saving buildings. E3S Web of Conferences, 563, 01003, (2024), https://doi.org/10.1051/e3sconf/202456301003

43. K.Turdibekov, M.Yakubov, A.Sulliev. Mathematical Models of Asymmetric Modes in High-Speed Traffic. Lecture Notes in Networks and Systems, 247, (2022), pp.1051-1058. DOI:10.1007/978-3-030-80946-1_95

44. A.Sanbetova, A.Mukhammadiev. Study on cultivation of environmentally friendly seed potatoes based on electrical technology. E3S Web of Conferences, 377, 03001, (2023), https://doi.org/10.1051/e3sconf/202337703001

45. M.Mirsadov, B.Fayzullayev, I.Abdullabekov, A.Kupriyanova, D.Kurbanbayeva, U.Boqijonov. The mutual influence of electromagnetic and mechanical processes in dynamic modes of inertial vibrating electric drives. IOP Conference Series Materials Science and Engineering, 862(6), 062081, (2020). doi:10.1088/1757-899X/862/6/062081

46. I.Abdullabekov, M.Mirsaidov, F.Tuychiev, R.Dusmatov. Frequency converter – asynchronous motor – pump pressure piping system mechanical specifications. AIP Conference Proceedings, 3152, 040007 (2024). https://doi.org/10.1063/5.0218880

47. I.Abdullabekov, M.Mirsaidov, Sh.Umarov, M.Tulyaganov, S.Oripov. Optimizing energy efficiency in water pumping stations: A case study of the Chilonzor water distribution facility. AIP Conference Proceedings, 3331, 030107, (2025). https://doi.org/10.1063/5.0305780

48. M.Bobojanov, F.Tuychiev, N.Rashidov, A.Haqberdiyev, I.Abdullabekov. Dynamic simulation of a three-phase induction motor using Matlab Simulink. AIP Conference Proceedings, 3331, 040012, (2025). https://doi.org/10.1063/5.0305750

49. M.Tulyaganov, Sh.Umarov, I.Abdullabekov, Sh.Adilova. Optimization of modes of an asynchronous electric drive taken into account thermal transient processes. AIP Conference Proceedings, 3331, 030084, (2025). https://doi.org/10.1063/5.0305786

50. Sh.Umarov, Kh.Sapaev, I.Abdullabekov. The Implicit Formulas of Numerical Integration Digital Models of Nonlinear Transformers. AIP Conference Proceedings, 3331, 030105, (2025), https://doi.org/10.1063/5.0305793

51. G.Boboyev, N.Inatova. The Importance of Implementing Energy Management Systems for Manufacturing Enterprises in the Republic of Uzbekistan. AIP Conference Proceedings, 3331(1), 040047, (2025). https://doi.org/10.1063/5.0305865

52. G.Boboyev, N.Nurmukhamedov, O.Zaripov. Improvement of Means of Measuring the Main Parameters of Electricity. AIP Conference Proceedings, 3331(1), 040039, (2025). https://doi.org/10.1063/5.0305861

53. A.T.Rakhmanov, G.G.Boboev. Developing the Technology for Manufacturing Ohmic Contacts and Sealing Semiconductor Temperature Converters. Journal of Engineering Physics and Thermophysics, 98(3), (2025), pp.841-845. https://doi.org/10.1007/s10891-025-03163-6

54. N.I.Avezova, P.R.Ismatullayev, P.M.Matyakubova, G.G Boboyev. Multifunctional Heat Converter Moisture Content of Liquid Materials. International Conference on Information Science and Communications Technologies Applications Trends and Opportunities Icisct 2019, 9012041, (2019). DOI: 10.1109/ICISCT47635.2019.9012041

55. J.Safarov, A.Khujakulov, Sh.Sultanova, U.Khujakulov. S.Verma. Research on energy efficient kinetics of drying raw material. E3S Web of Conferences, 216, 01093, (2020). https://doi.org/10.1051/e3sconf/202021601093

56. J.Safarov, Sh.Sultanova, G.Dadayev, Sh.Zulponov. Influence of the structure of coolant flows on the temperature profile by phases in a water heating dryer. IOP Conf. Series: Materials Science and Engineering, 1029(1), 012019, (2021). doi:10.1088/1757-899X/1029/1/012019

57. Sh.Sultanova, A.Artikov, Z.Masharipova, A.Tarawade, J.Safarov. Results of experiments conducted in a helio water heating convective drying plant. IOP Conf. Series: Earth and Environmental Science, 868(1), 012045, (2021). doi:10.1088/1755-1315/868/1/012045

58. Sh.Sultanova, J.Safarov, A.Usenov, D.Samandarov, T.Azimov. Ultrasonic extraction and determination of flavonoids. AIP Conference Proceedings, 2507, 050005, (2023). https://doi.org/10.1063/5.0110524

59. Dj.Saparov, S.Sultonova, E.Guven, D.Samandarov, A.Rakhimov. Theoretical study of characteristics and mathematical model of convective drying of foods. E3S Web of Conferences, 461, 01057, (2023). https://doi.org/10.1051/e3sconf/202346101057

60. Sh.Sultanova, J.Safarov, A.Usenov, T.Raxmanova. Definitions of useful energy and temperature at the outlet of solar collectors. E3S Web of Conferences, 216, 01094, (2020). https://doi.org/10.1051/e3sconf/202021601094

61. Sh.Zulpanov, D.Samandarov, G.Dadayev, S.Sultonova, J.Safarov. Research of the influence of mulberry silkworm cocoon structure on drying kinetics. IOP Conf. Series: Earth and Environmental Science, 1076, 012059, (2022). doi:10.1088/1755-1315/1076/1/012059

62. A.Tarawade, D.Samandarov, T.Azimov, Sh.Sultanova, J.Safarov. Theoretical and experimental study of the drying process of mulberry fruits by infrared radiation. IOP Conf. Series: Earth and Environmental Science, 1112, 012098, (2022). doi:10.1088/1755-1315/1112/1/012098

63. S.M.Turabdzhanov, J.M.Tangirov, P.M.Matyakubova, N.S.Amirkhulov, S.S.Khabibullaev. Methods of providing metrological supply when pumping water into wells in oil fields. AIP Conference Proceedings, 3045(1), 030073, (2024), https://doi.org/10.1063/5.0197355

64. S.J.Nimatov, D.S.Rumi. Investigation of the dose dependence of the amorphization of a Si(111) surface bombarded with low-energy Na+ ions. Journal of Surface Investigation, 8(2), (2014), pp.404-407. DOI: 10.1134/S1027451014020396

65. S.J.Nimatov, D.S.Rumi. Submonolayer films on a Si(111) surface under low-energy ion bombardment. Bulletin of the Russian Academy of Sci. Physics, 78(6), (2014), pp.531-534. DOI: 10.3103/S1062873814060215